POWER FLOW CONTROL USING TCSC

(THYRISTOR CONTROLLED SERIES CAPACITOR)

A dissertation submitted in partial fulfillment of the requirement for the award of the degree of

Master of Engineering

in

Electrical Engineering

(Power Apparatus and System Engineering)

By

BIJOY KUMAR SAHOO

University Roll No-9091

Under the Guidance of

Dr. Narendra Kumar

Professor

Department of Electrical Engineering

Delhi College of Engineering

University of Delhi

2005-2006

CERTIFICATE

This is to certify that the dissertation entitled, “POWER FLOW CONTROL USING TCSC (THYRISTOR CONTROLLED SERIES CAPACITOR)” which is being submitted by Bijoy Kumar Sahoo in partial fulfillment of the award of M.E. Degree in Electrical Engineering with specialization in ‘Power Apparatus and System Engineering’, is a record of students own work carried out by him under my guidance and supervision. The matter embodied in this dissertation has not been submitted for the award of any degree to the best of my knowledge and belief.

(Dr. Narendra Kumar)

Professor

Dept. of Electrical Engineering

Delhi College of Engineering, Delhi

ACKNOWLEDGEMENT

I express sincere thanks and deep sense of gratitude to my Project Guide Dr. Narendra Kumar, Professor, Department of Electrical Engineering, Delhi College of engineering,  for his motivation and guidance, without which this project wouldn’t have been possible. I consider myself fortunate for having the opportunity to learn and work under his able supervision and guidance over the entire period of association with him. I have deep sense of admiration for his innate goodness.

Also I am deeply thankful to Dr Parmod Kumar, (HOD), Department of Electrical Engineering for his valuable advice for the project. At the same time I am thankful to Professor SP Seth (Retd), Mr. Sumon Bhowmic (Lecturer) and Mr. T Nagrajan (Lecturer) to help me out by providing necessary tips on the subject.

I would thank my wife Kumudini for her constant encouragement, and my two and a half year old son Biswajeet who suffered some alienation and negligence during the course of this work. I acknowledge the support and contribution of my colleagues Mr. S.K. Jha , Lecturer, NSIT, Delhi who believe in the collective pursuit of knowledge and was ever ready to help me with information and suggestions.

Lastly, my deepest gratitude to Almighty God whose divine light provided me the perseverance, guidance, inspiration and strength to complete this work.

This is to acknowledge that, the dissertation has been completed under the AICTE R & D Project, “Enhancing Power System Performance using FACTS Devices” in the Flexible AC Transmission systems (FACTS) Lab.

(Bijoy Kumar Sahoo)

University Roll No-9091

CONTENTS

Page No

Abstract									1

Chapter-1	Introduction							2-3

Chapter-2	Literature Review						4-6

Chapter-3	Concept of Active and Reactive Power Flow 		7-16

3.1	Active and Reactive Power Flow			7

3.2	Analysis of Power Flow using PSCAD-4.0		9

Software

3.3	Power Flow Analysis of two bus network		10

(Simulink Block)

3.4	Conclusion						16

Chapter-4	Power Flow Analysis						17-21

4.1	Principle of Power Transmission			17

4.2	Controllable Parameter				21

4.3	Conclusion						21

Chapter-5	Series Compensation						22-27

5.1	Principle of  Series Compensation			22

5.2	Simulation Block for Capacitive Compensation	25

5.3	Types of Series Compensator				27

5.4	Conclusion						27

Chapter-6	Thyristor-Controlled Series Capacitor (TCSC)		28-49

6.1	Introduction						28

6.2	Thyristor-Controlled Reactor				28

6.3	Physical Model of TCSC				30

6.4	Modes of operation					31			6.5	Analysis of TCSC Equivalent Circuit			32

6.6	Simulation of TCSC Circuit using PSCAD-4.0	37

6.7	TCSC Steady State Characteristics			39

(Simulink Block)

6.8	Dynamic Characteristics of TCSC			42

(Open Loop Control)

6.9	Simulink Block for TCSC Closed Loop Control	45

6.10	Power Flow Control Using TCSC			47

(Simulink Block)

6.11	Conclusion						49

Chapter-7	Power Flow Solution of Large Electrical Network	50-70

7.1	Objective						50

7.2	Power Flow Solution					50

7.3	Bus Admittance Matrix				51

7.4	Power Flow Equation					52

7.5	Power Mismatch Equation				55

7.6	Net Active and Reactive Power			56

7.7	Variables and Bus Type				56

7.8	Power Flow Solution Method				57

7.9	Newton-Raphson Algorithm				57

7.10	Newton-Raphson method for				59

Power Flow Problem

7.11	State Variable Initialization				61

7.12	Generator Reactive Power Limit			62

7.13	Generalized Power Flow Solution			62

for 5-Bus Network

MATLAB Program-5.1				65

Summary of Output					68

7.14	Conclusion						69

Chapter-8	Power Flow Control Using TCSC				71-93

8.1	Active and Reactive Power Flow through TCSC	71

8.2	Power Flow Solution for 6-Bus Network		74

MATLAB Program-6.1				77

Summary of Output					81

8.3	Power Flow Solution of 7-Bus Network		84

MATLAB Program-6.2				87

Summary of Output					90

8.4	Conclusion						93

Chapter-9	Conclusion and Further Scope of work			94-95

9.1	Summary of work					94

9.2	Conclusion						95

9.3	Further Scope of Work				95

Appendix – A		MATLAB Program-2.1				96

MATLAB Program-4.1				96-97

Appendix – B		MATLAB Program-5.1				98-102

Appendix – C		MATLAB Program-6.1				103-107

References									108-109

ABSTRACT:

In this project work a review of the salient features of Power Flow Control using TCSC are elegantly discussed. This dissertation has been organized into nine chapters where first Chapter describes the need of power flow control. Chapter 3rd and 4th describes the concept of active and reactive power flow and the Principle of power flow in transmission line, its analysis with controllable parameter such as load angle, line impedance, and terminal voltage. PSCAD-4.0 / MATLAB Program are used to observe the variation of active and reactive power flow with different variable parameters and set of data. For each set of data, output result is obtained. In the next two Chapters, Principle of series compensation and TCSC with its dynamic characteristics and active power flow control using TCSC with software simulation has been delineated. The consequent remaining Chapters mainly deals with Load flow solution of a 5-bus network by using Newton-Raphson method and power flow control using TCSC, in which the original 5-bus network is modified to 6-bus / 7-bus network to accommodate one TCSC / two  TCSC. The load flow solution is found for the modified 6-bus / 7-bus network. The result of load flow solution shows that the specified amount of active power flow is controlled by the use of TCSC. The salient feature of the dissertation is the fact that MATLAB and PSCAD-4.0 has been thoroughly used to investigate the different aspects of  power flow control.

1

INTRODUCTION

1.1	NEED OF POWER FLOW CONTROL:

Electrical networks are interconnected to different generating stations and load centers according to the existing plan. But load demands on the system are not constant. With the increase of industrial growth and domestic load, more power is consumed by the different loads. To fulfill the load demand, either electrical system network to be re-evaluated or the power carrying capability of the transmission line to be increased. Economic point of view, modification or alteration of electric network is costly. Thus aim is to increase the power carrying capability of transmission line.

1.2	HOW TO CONTROL POWER FLOW :

The various parameters involved in power flow are [3][6]:

(a) load angle

(b) Transmission line impedance

(c) Operating variables such as voltage and current

To control the power flow from one bus to another bus, either of three parameters to be controlled.

Power systems of today are mechanically controlled. Mechanical switching action is slow and power flow control is not fast enough according to the load variation. Another problem of mechanical control is that it cannot be initiated frequently as it leads to wear and tear.

To maintain both dynamic and steady state operation, the new technology i.e FACTS  (Flexible ac Transmission System) is used which is a power electronics based system. Its main role is to enhance controllability and power transfer capability in ac systems. FACTS technology uses switching power electronics to control power flow in the range of few tens to a few hundreds of megawatts.

The various FACTS controller are capable of controlling the interrelated line parameters and other operating variables as mentioned in this paragraph. Thus FACTS controller govern the operation of transmission system by providing series impedance, shunt impedance, line current, voltage, phase angle and damping of oscillations at various frequencies below the rated frequency. By providing added flexibility, FACTS controllers can enable a transmission line to carry power

- Up to its thermal rating

- By maintaining proper insulation of transmission line without over-voltage.

- By maintaining stability in the system

Thus  use of FACTS technology increases the power carrying capability of existing transmission network which is more economical.

1.3	VARIOUS FACTS CONTROLLERS [3]:

In general FACTS controllers can be divided into four categories:

- Series Controller

- Shunt Controller

- Combined series-series Controllers

- Combined series-shunt Controllers

In this project, it is considered about  one of  the Series Controller that is Thyristor Controlled Series Capacitor  (TCSC) to control the power flow  in the transmission line.  TCSC is one of the FACTS devices which consist of a series capacitor bank shunted by a thyristor-controlled reactor in order to provide a smoothly variable series capacitive reactance by varying the firing angle of  Thyristor-controlled reactor.

1.4	OBJECTIVE AND SCOPE OF DISSERTATION:

With the objective of controlling the power flow in the transmission line using TCSC, it is essential to know the power flow between two buses and the various parameters involved in the power flow equation. Power Electronic Control in Electrical Systems offers a solid theoretical foundation for the electronic control of active and reactive power in the transmission line. Thus use of Flexible AC transmission System FACTS controller, has strong impact on power flow control.

2

LITERATURE REVIEW

A review of earlier paper published on the FACTS controller shows that a lot of work done on different FACTS controller. Also several papers published on Thyristor Controlled Series Capacitor (TCSC) which is used for different application as mentioned below. Still a lot of work to be done to improve the power flow control in long transmission line.

2.1	APPLICATION OF TCSC [13]:

(a)	Continuous control of the transmission line series compensation level.

(b)	Dynamic control of power flow in selected transmission lines within the network to enable optimal power flow condition.

(c)	Damping of the power swings from local and inter area oscillations.

(d)	Suppression of sub-synchronous oscillations.

(e)	Enhanced level of protection for series capacitors.

(f)	Voltage regulation by generating reactive power.

(g)	Reduction of the short-circuit current.

2.2	VARIOUS WORKS ON DIFFERENT APPLICATIONS:

Fuerte-Esquivel, C.R.; Acha, E.; Ambriz-Perez, H. [8]  presented a paper on TCSC model for the power flow solution of practical power networks in which power flow from one bus to another bus is determined. In this paper he discussed how TCSC can be incorporated  into electrical network having large number of buses. Also he found load flow solution using Newton-Raphson method within the specified tolerance.

R. Mohan Mathur, Rajiv K Verma , IEEE Press Series on Power Engineering,2002 [13] , discussed the various applications of TCSC such as improvement in system stability, the damping of power oscillations, the alleviation of sub-synchronous resonance (SSR) and the prevention of voltage collapse. In addition, he described about two TCSC’s installation : one in Sweden, the other in Brazil.

P.H. Ashmole described in IEE publication [6] about the FACTS controllers and its utility. In his discussion in “Introduction to FACTS” he described that FACTS controller are mainly aim to control three parameters such as voltage, phase angle and impedance. According to him the various advantages of the FACTS devices are :

(a)	Potential to control flows as required

(b)	Less environmental impact than most alternative techniques of transmission reinforcement .

(c)	Depending on the cost benefit analysis could cost less than other alternatives.

Also he described about the various FACTS controller, in which TCSC is one of the

FACTS controller. Development stage of various FACTS controllers also presented in that publications.

Jonas Person, Lennart Soder [15][18] developed a linear model for TCSC and he found that simulation with linear model takes few secs as compared to actual model takes an hour to complete.

Narain G. Hingorani, Laszlo Gyugyi, [3] has described about all FACTS controller in his book “Understanding FACTS”. Out of many FACTS controller TCSC is one of the important FACTS controller about which he described in details how its range of reactance varies from inductive to capacitive region.

Persson, J.; Rouco, L.; Soder, L, [18] present a related topic on Linear analysis with two linear models of a thyristor-controlled series capacitor at Power Tech Conference Proceedings, 2003 IEEE Bologna.

Abdel-Moamen, M.A.; Padhy, N.P, [12] presented a paper on Multi-objective optimal power flow model with TCSC for practical power networks at Power Engineering Society General Meeting, 2004. In this paper he has discussed how the transmission line loss in a 30-bus system can be minimized using Newton’s method.

Xiaobo Tan and Luyuan Tong presented a paper on “Characteristics and Firing angle control of Thyristor Controlled Series Compensation installations” [23] . This paper studies two important aspects of TCSC characteristics, the time constant of TCSC dynamic response and impacts of reference signals for thyristor firing angles on TCSC dynamic response. A two stage firing control method is presented to accomplish smooth switching between the capacitive region and inductive region. EMTDC/PSCAD software is used to analyze the behavior of TCSC circuit.

R. Billinton, M. Fotuhi-Firuzaba and S.O. Faried describe the impact of a Thyristor Controller Series Capacitor (TCSC) on power system reliability [24] . In this application the TCSC is employed to adjust the natural power sharing of two different parallel transmission lines and therefore enable the maximum transmission capacity to be utilized. A reliability model of a multi-module TCSC has been developed and incorporated in the transmission system. The result of the investigation shows a significant improvement in the system reliability when the TCSC is utilized.

Zhao Xueqiang and Chen Chen, senior member IEEE developed mathematical equations of TCSC for any period of time (including the whole transient process from firing the thyristos to a study to a steady state) [25] . The accurate mathematical relationship between fundamental impedance of TCSC and the firing angle of the thyristor is further derived by using Fourier analysis. The validity of the mathematical analysis is demonstrated by using the Electro-Magnetic Transient Program (EMTP) digital simulations. The test result agrees well with the analytical and simulation results and clarifies the validity of the assumption that the line current keeps sinusoidal, which is taken both in the mathematical analysis and the EMTP digital simulations.

A.Ally and B.S Rigby, member of IEEE, investigated the impact of TCSC to improve the small signal and transient stability under fault condition [22] . Both the constant power and constant angle modes power flow control are examined for a range of controller response time. The result indicates that the effect of  a power flow controller on system stability is dependent on both the mode of the controller and its response time.

The research work is unending on Thyristor Controlled Series Capacitor to improve it characteristics and to apply in many more electrical technology to improve the power flow stability, power flow control and in related applications.

3

CONCEPT OF ACTIVE AND

REACTIVE POWER FLOW

R + j X

Ss = Ps + jQs

Sr = Pr + jQr

Load

Generator

Is

Ir

Two Bus System

Fig 3.1

3.1	ACTIVE AND REACTIVE POWER FLOW [1][4]:

From fig 3.1 which is a two bus system connected two generators and one load

Let

Is = Sending end current

Ir = Receiving end current

Es = Sending end voltage =  Vs∠δ

Er = Receiving end voltage = Vr∠0

R=Transmission line resistance

X= Transmission line reactance

Transmission line impedance Z = R + jX = Z∠α

Sending end current Is=Vs∠δ−Vr∠0Z∠α

Is=Vs ∠δ−αZ−Vs∠−αZ

Ss = Sending end complex power = Vs Is*

Ss=Vs∠δVs ∠α−δZ−Vs∠αZ

Ss=Vs2∠αZ−VsVr∠α+δZ (3.1)

Real power  or active power flow from sending end is

Ps =  Real (Ss)

Ps=Vs2 cos αZ−VsVr cosα+δZ (3.2)

Reactive power at sending end is

Qs = Imaginary (Ss)

Qs=Vs2 sin αZ−VsVr sinα+δZ (3.3)

Power system transmission lines have small resistance compared to the reactance i.e R/X ratio is very small. Also power loss in the transmission line is negligible. Thus with this assumption

R = 0, Z=X∠90

i.e   α = 900

So equations (3.2) and (3.3) becomes

Ps=VsVrXsin δ (3.4)

Qs=VsXVs−Vr cos δ (3.5)

From the equations (3.4) and (3.5), it is clear that for a typical power system with small R/X ratio, the following important observations are made :

1. 	Equ (3.4) shows that flow of real power from sending end is proportional to sin δ. That is with small change in phase angle between sending end and receiving end voltage has significant effect on the real power flow. But small changes in voltage magnitude will not have appreciable effect on the real power flow.

If Es leads Er, then load angle  δ is positive and real power flows from sending end to receiving end.

If Es lags Er, then load angle δ is negative and power flows from receiving end to sending end.

2.	If  resistance  R = 0 , then maximum real power flow from sending end occurs at δ = 900

The maximum power flow is given by Pmax=VsVrX

3. 	For maintaining transient stability, the power system is usually operated with small load angle δ. Thus cos δ ≈ 1 for δ is very very small. Thus reactive power flow from sending end for small δ is given by :

Qs=VsXVs−Vr

Thus reactive power flow from sending end to receiving end is affected very much with small voltage difference between sending end and receiving end voltage.

3.2	ANALYSIS OF POWER FLOW  USING PSCAD- 4.0 SOFTWARE :

Using PSCAD software, we will analysis how power flow from one end to other end of a two bus system can be controlled or varied. The various parameters involved for power flow control are:

(a) Load angle ( δ)

(b) Transmission line impedance variation (Z)

(c) Voltage variation between two ends

3.3	POWER FLOW ANALYSIS OF TWO BUS NETWORK :

(SIMULINK BLOCK)

Fig-3.2

CASE-1

Following data are assumed for the purpose of simulation of simple two bus network to analyze the power flow from one bus to another.

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 300

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0223 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-1:

CASE-2

(Variation of load angle i.e load angle is increased with respect to CASE-1)

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 400

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0223 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-2:

From the result it is clear that with the increase of sending end phase angle from 300 to 400, there is increase of active power flow from sending end to receiving end(Psr) i.e. 2753.25 watt to 3542.34 watt

CASE-3

(Variation of load angle i.e load angle is decrease with respect to CASE-1)

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 200

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0223 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-3:

From the result it is clear that with the decrease of sending end phase angle from 300 to 200, there is decrease of active power flow from sending end to receiving end(Psr) i.e. 2753.25 watt to 1906.71 watt

CASE-4

(Variation of line impedance; i.e increasing the inductance with respect to CASE-1)

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 300

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0723 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-4:

From the result it is clear that with the increase of line inductance from 0.0223 H to 0.0723 H, there is decrease of active power flow from sending end to receiving end(Psr) i.e. 2753.25 watt to 812.436 watt

CASE-5

(Variation of line impedance; i.e decreasing the inductance with respect to CASE-1)

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 300

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0198 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-5:

From the result it is clear that with the decrease of line inductance from 0.0223 H to 0.0198 H, there is increase of active power flow from sending end to receiving end(Psr) i.e. 2753.25 watt to 3118.45 watt

CASE-6

(Variation of terminal voltage as compared to CASE-1)

Vs = magnitude of sending end voltage

= 173 volts (line to line)

δs = phase angle of sending end = 300

Vr = magnitude of receiving end voltage

= 208 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0223 Henry per phase

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT FOR CASE-6:

From the result it is clear that reactive power flow from receiving end is increased to 2345.27 var as receiving end voltage is more than that of sending end as compared to CASE-1. In CASE-1, sending end voltage is more than receiving end voltage. Thus reactive power flows from sending end.

3.4		CONCLUSION:

From the above simulation result using PSCAD, it is clear that power flow in the transmission line varies with various parameters such as load angle, line impedance and terminal voltage. So power flow control involves the control of various parameters such as load angle, transmission line impedance and terminal voltage.

4

POWER FLOW ANALYSIS

4.1	PRINCIPLE OF POWER TRANSMISSION

To understand the principle of power transmission it is essential to represent the transmission line. Transmission line can be represented by a series reactance with the sending end and receiving end voltages [2]. This is shown in figure below for one phase of three phase system and all quantities such as voltage and currents are defined per phase.

jX/2

jX/2

+

Vs

-

+

Vm

-

+

Vr

-

I

(a)Two-machine power system

Vr

Vs

I

Vm

Vx=jXI

(b) Phasor diagram

δ/2

δ/2

FIGURE 4.1

From Fig 4.1(a),

Let Vs = per phase sending end voltage magnitude

Vr = per phase receiving end voltage magnitude

Vm = per phase mid point voltage magnitude

jX/2 = Thevenin equivalent impedance located on the right or left side of

the mid point

δ = Phase angle between sending and receiving end voltage

let us assume that the magnitude of the terminal voltages remain constant and equal to V. That is

Vs = Vr = V

The two terminal voltages can be expressed in phasor notations in rectangular coordinates as follows

Vs = V e j δ/2 = V (cos δ/2 + j sin δ/2)					 (4.1)

Vr = V e- j δ/2 = V (cos δ/2 + j sin δ/2) 				 (4.2)

So Vm is equal to average value of Vs and Vr as given by

Vm=Vs+Vr2=Vm ej0=Vcosδ2∠00 				 (4.3)

The line current phasor is given by

I=Vs−VrX=2VXsinδ2∠900 					       (4.4)

where the magnitude of │I│ is I = 2V/X  sin δ/2 .

For lossless line, the power is same at both ends and at the midpoint. Thus active power at sending end ( Ps) is equal to the active power at the mid point (Pm) and also equal to the active power at  receiving end (Pr).

Ps=Pr=Pm=VmI

Applying the value of magnitude of Vm from equ. (4.3) and the value of line current I from equ. (4.4)

Ps=Pr=Pm=Vcosδ2×2VXsinδ2=V2Xsinδ  (4.5)

The reactive power at the receiving-end Qr is equal and opposite of the reactive power Qs supplied by the sources. Thus the reactive power Q for the line is given by

Q=Qs=Qr=VIsinδ2

Applying the value of current I in above expression we get,

Q=Qs=Qr=V×2VXsinδ2×sinδ2=V2X1−cosδ (4.6)

From the above analysis it is clear that active power flow becomes maximum

Pmax = ( V2 / X) at δ = 900

And the reactive power  becomes the maximum

Qmax = (2V2 / X) at δ =1800

By writing a small MATLAB program we will analyze how the load angle δ control both the active power demand and reactive power demand on sending end and receiving end. Also we will see how reactive power demand changes with the any changes in active power flow.

MATLAB PROGRAM 2.1

%ANALYSIS OF ACTIVE AND REACTIVE POWER FLOW IN A LOSS LESS TRANSMISSION LINE

(Attached in appendix-‘A’)

After execution of this program, we come to know that load angle δ is an parameter to control the both active and reactive power according to load demand.

DATA USED :

line voltage= 220 V

line reactance= 1.2 ohm

RESULT IS :::::

delta           P            Q

1.0e+004 *  (watt)     (var)

0          0             0

0.0010    0.7004    0.0613

0.0020    1.3795    0.2432

0.0030    2.0167    0.5404

0.0040    2.5926    0.9436

0.0050    3.0897    1.4408

0.0060    3.4930    2.0167

0.0070    3.7901    2.6539

0.0080    3.9721    3.3330

0.0090    4.0333    4.0333 (P=Q=Pmax)

0.0100    3.9721    4.7337

0.0110    3.7901    5.4128

0.0120    3.4930    6.0500

0.0130    3.0897    6.6259

0.0140    2.5926    7.1230

0.0150    2.0167    7.5263

0.0160    1.3795    7.8234

0.0170    0.7004    8.0054

0.0180    0.0000    8.0667(P=0, Q=2Pmax)

δ→

δ→

Fig- 4.2

4.2	CONTROLLABLE PARAMETER :

From the  above discussion it is clear that the power and current in the transmission line can be controlled by the following means [2][3] :

- Applying a voltage in the midpoint can increase an decrease the magnitude of power.

- Applying a voltage in series with the line, and in phase quadrature with the current flow, can increase or decrease the magnitude of current flow. As the current flow lags the voltage by 900 ,there is injection of reactive power in series.

- If a voltage with variable magnitude and a phase is applied in series, then varying the amplitude and phase angle can control both active and reactive power. This requires injection of both active power and reactive power in series.

- Increasing and decreasing the value of the reactance X can also decrease and in crease the power height of both active and reactive power.

- Power flow can also be controlled by regulating the magnitude of sending and receiving end voltages Vs and Vr. This type of control has much influence on reactive power flow than active power flow.

4.3	CONCLUSION:

From the above MATLAB analysis, we come to know that how the active and reactive power varies with the load angle. Analysis clearly shows that the plotted graph which is obtained from the execution of MATLAB code resembles with curve drawn in different books by different author. In this curve we come to know, as we vary the line reactance, the height of active power curve varies.

5

SERIES COMPENSATION

5.1	PRINCIPLE OF SERIES COMPENSATION :

A voltage in series with the transmission line can be introduced to control the current flow and thereby the power transmissions from the sending end to the receiving end [2]. An ideal series compensator is represented by the voltage source Vc which is connected in the middle of a transmission line as shown in Fig. 5.1(a)

jX/2

jX/2

+

Vs

-

+              +

Vm1       Vm2

-                -

+

Vr

-

Ideal series

Compensator

Vc

I                               +         -                            I

(a)Two-machine power system

jX/2

jX/2

+

Vs

-

+

Vm

-

+

Vr

-

I

(b)Two-machine power system

-jXc/2

-jXc/2

Vr

Vs

I

Vm

Vx

(c) Phasor diagram

δ/2

δ/2

FIGURE 5.1

-jXc/2I

-jXc/2I

From Fig-5.1 (a),

Let Vs = per phase sending end voltage magnitude

Vr = per phase receiving end voltage magnitude

Vc = per phase mid point voltage magnitude  is applied in series

X = Transmission line impedance

δ = Phase angle between sending and receiving end voltage

Assuming Vs = Vr = Vc = V

The current flowing through transmission line is given by

I=Vs−Vr−VcjX								(5.1)

If the series applied voltage Vc is in quadrature with respect to the line current, the series compensator cannot supply or absorb active power. This is because phase angle between voltage and line current is 900 (i.e cos 900=0). Thus the power at the source Vc terminal can be only reactive. This means that capacitive or inductive equivalent impedance may replace the voltage source Vc.

So equivalent transmission line impedance of compensated line can be represented by

Xeq=X−Xcomp=X(1−r) 							(5.2)

where r=XcompX

and r is the degree of series compensation and its range is 0≤r≤1  and

Xcomp is the series equivalent compensation reactance which is positive if it is capacitive and negative if it is inductive.

The magnitude of the current through the line is given by using equ. (4.4)

I=Vs−VrXeqI=2V(1−r)Xsinδ2								  (5.3)

The active power flowing through transmission line is given by using equ.(4.5)

Pc=VcI=V2Xeqsinδ=V21−rXsinδ 					  (5.4)

The reactive power Qc at the source Vc terminal is given by using equ (4.6)

Qc=I2Xcomp=2V2X×r1−r21−cosδ 					  (5.5)

For capacitive compensation the line current leads the voltage Vc by 900 whereas for inductive compensation the line current lags the Vc by 900.

Series capacitive impedance decreases the overall transmission  line impedance and thereby increases the transmittable power. Whereas series inductive impedance increases the overall transmission line impedance, thus decreases the transmittable power.

Principle of series compensation is analyzed by using a series capacitor in transmission line and this is analyzed with the help of PSCAD-4.0 software as given below

5.2	SIMULATION BLOCK FOR CAPACITIVE COMPENSATION:

Fig-5.2

DATA FOR THE SIMULATION BLOCK (Fig-5.2) :

Vs = magnitude of sending end voltage

= 208 volts (line to line)

δs = phase angle of sending end = 300

Vr = magnitude of receiving end voltage

= 173 volts (line to line)

δr = phase angle of receiving end = 00

R  = resistance of line = 1 ohm per phase

L  = inductance of line = 0.0223 Henry per phase

C  = compensation capacitor = 1200 micro farad

Psr = Active power flow from sending end to receiving end

Prs = Active power flow from receiving end to sending end

Qsr = Reactive power flow from sending end to receiving end

Qrs = Reactive power flow from receiving end to sending end

SIMULATION RESULT WITHOUT SERIES CAPACITOR:

SIMULATION RESULT WITH SERIES CAPACITOR :

From the result it is clear that active power flow from sending end is increased from 2753.25 watt to 4523.73 watt with the use of  1200 micro farad series capacitor.

5.3	TYPES OF SERIES COMPENSATOR [2]:

- Thyristor-switched series capacitor

- Thyristor-controlled series capacitor

- Forced-commutation-controlled series capacitor

- Series static VAR compensator

- Advanced SSVC

Out of these series compensator, Thyristor-controlled series capacitor (TCSC)  is discussed in the next chapter and a MATLAB program is used for it to analyze, how it control the power flow.

5.4	CONCLUSION:

From the PSCAD simulation result, we concluded that use of capacitor in the transmission line will provide series compensation of the transmission line. By varying the capacitor value, we can change the power transfer capability of the transmission line.

6

THYRISTOR-CONTROLLED

SERIES CAPACITOR

(TCSC)

6.1	INTRODUCTION:

The TCSC varies the electrical length of the compensated transmission line with little delay [7]. Owing to this characteristic, it may be used to provide fast active power flow regulation. It also increases the stability margin of the system and has proved very effective in damping Sub-Synchronous Resonance (SSR) and power oscillation. The TCSC is the parallel combination of Thyristor Controlled reactor (TCR)  and a fixed capacitor. So before discussing in details about TCSC, let us discuss about TCR.

6.2	THYRISTOR-CONTROLLED REACTOR (TCR) [2] :

It consists of a fixed reactor of inductance L and a bidirectional thyristor switch SW as shown Fig 6.1

iL(α)

SW

FIGURE-6.1

The current through the reactor can be controlled from zero (when the switch is open) to maximum (when the switch is closed) by varying the firing angle α of the thyristor. Thus the conduction angle of the thyristor is σ = π - 2α. If the switch is permanently closed when  α = 0, then it has no effect of the inductor current.

Let the supply voltage v(t)=Vm cos wt = 2 V cos wt

where Vm = peak voltage of supply voltage

Thus instantaneous inductor current can be expressed as a function of α as follows :

iL(t)=1Lαwtv(t)dt=1wLVm sin wtαwt=VmwL(sinwt − sin α)			 (6.1)

which is valid for  α≤wt≤π−α

From the equation (6.1) it is clear that iL(t) is maximum when α = 0 and it is zero when α = π/2.

The fundamental root-mean-square (rms) current of the reactor can be found as

ILFα=VwL1−2πα−1πsin2α						  (6.2)

which is α (firing angle) dependent

Thus admittance for the shunt compensator for fundamental current is given by

YLα=ILFV=1wL1−2πα−1πsin 2α					   (6.3)

The impedance of compensator

ZL(α)=1YLα=VILF=wL1−2πα−1πsin2α 				   (6.4)

which is dependent on α.

6.3	PHYSICAL MODEL OF TCSC :

Vc(α)

I                   +     -              ic(α)= i + iL(α)

L

SW

FIGURE - 6.2

Thyristor-controlled series capacitor(TCSC)

The TCSC consists of the series-compensating capacitor shunted by a thyristor-controlled reactor (TCR) as shown in fig. 6.2.[2][3]. The impedance of the reactor XL is sufficiently smaller than that of the capacitor impedance Xc is taken. By varying the delay angle or firing angle(α) of TCR, the inductive impedance of TCR can be varied. Thus TCSC can provide variable capacitance by means of canceling the effective capacitance by the TCR. Therefore, the steady state impedance of TCSC is simply that of the parallel LC circuit, consisting of fixed capacitive impedance Xc and variable inductive impedance XL.

The effective impedance of the TCSC is given by

XTα=XcXLαXLα−Xc 								(6.5)

where XL(α) is the variable impedance of TCR which can be taken from equ.(6.4)

that is

XLα=XLππ−2α−sin2α           for XL≤XLα≤∞ 				(6.6)

where XL=ωL and α is the delay angle measured from the crest of the capacitor voltage or the zero crossing of the line current.

The TCSC behaves as a tunable parallel LC-circuit to the line current. As the impedance of the controlled reactor XL(α) is varied from its maximum (infinity) toward its minimum (ωL) i.e. when α varies from 900 to 00, then TCSC increases its minimum capacitive impedance XTmin=Xc=1ωC, until parallel resonance occurs at Xc=XLα and XT(α) approaches to it maximum value XT(max)=infinite. If we decrease XL(α) further, the XT(α) becomes inductive and approaches to its minimum value of XT(min)=XcXL/(XL-Xc) at α=00. i.e the effect of capacitor is bypassed by TCR.

Angle α has two limiting values (1) one for inductive α L(lim) and

(2) one for capacitive αC(lim).

The TCSC has two operating ranges around its internal circuit resonance :

(1) one is the αClim≤α≤π2 range, where XT(α) is capacitive

(2) the other is the 0≤α≤αLlim range, where XT(α) is inductive.

6.4	MODES OF OPERATION [7][13] :

The TCSC has three fundamental modes of operation as follows :

(a)	Thyristor-blocked mode : In this mode of operation, the current through the TCR is zero and the TCSC function as a capacitive reactance Xc  .

(b)	Thyristor-bypassed mode : In this mode, the thyristor valves are fired with no delay and the TCSC has small inductive impedance.

(c)	Thyristor- phase controlled mode : In this mode the value of the firing angle determines the direction of the current through the TCR and the capacitor, enabling the TCSC to work as either a capacitive or an inductive reactance. In this mode, the thyristor firing mechanism is controlled to vary the amount of effective reactance connected to the system .

6.5		ANALYSIS OF THE TCSC EQUIVALENT CIRCUIT :

iT(t)

iS(t)

Fig 6.3   Simplified TCSC Circuit

The analysis of TCSC operation in the vernier-control mode is performed based on the simplified TCSC circuit as shown in Fig. 6.3.[8] [13][25]

From the Fig-6.3

iS(t) = Transmission line current which is modeled as an external current source and assumed to be sinusoidal current.

iT(t) = Thyristor-valve current

u = switching variable

when u =1, thyristor is conducting i.e. switch S is closed

when u = 0, thyristor is blocked i.e switch S is open

C = Fixed capacitor used in parallel with TCR circuit

L =  Inductance used in series with Thyristor bidirectional switch

Vc(t) = voltage across the capacitor C

The current through the fixed capacitor C is expressed as

Cdvcdt=iSt−iTt⋅u  														(6.7)

The current through thyristor is given by

LdiTdt=vC⋅u  																 (6.8)

Let the line current iS(t) be represented by

iSt=Imcoswt  																(6.9)

In equidistant firing-pulse control, for balanced TCSC operation, the thyristors are switched on twice in each cycle of the line current at instants t1 and t3  and these are given by

t1=−βw

t3=π−βw

where  β is the angle of advance (before the forward voltage becomes zero) or,

β=π−α;		0<β<βmax

where  α is the firing angle of  the thyristor. This angle is generated using a reference signal that can be in phase with the capacitor voltage. The thyristor switch S turns off at the instants t2 and t4 , defined as

t2=t1+σw

t4=t3+σw

where  σ is the conduction angle, which is assumed to be the same in both the positive and the negative cycle of conduction. Also,

σ=2β

Solving the TCSC equations ( 6.7)-(6.9) results in the steady state thyristor current iT, as

iTt=ϖ2ϖ2−2Imcoswt−cosβcosϖβcoswrt; −β≤wt≤β  				(6.10)

where wr is called resonance frequency and is given by

wr=1LC  and

ϖ=wrw=XCXL12

where XC and XL are capacitive reactance and inductive reactance respectively.

The steady state capacitor voltage at the instant wt=−β is expressed as

vC1=ImXCϖ2−1sinβ−ϖcosβtanϖβ 										(6.11)

At wt=β, iT=0, the capacitor voltage is given by

vC(wt=β)=vC2=−vC1  													(6.12)

Finally the capacitor voltage is given by

vCt=ImXCϖ2−1−sinwt+ϖcosβcosϖβsinwrt; −β≤wt≤β  				(6.13)

vCt=vC2+ImXC(sinwt−sinβ); β<wt<π−β   					(6.14)

Because the non-sinusoidal capacitor voltage,  vc, has odd symmetry about the axis

wt = 0, the fundamental component, VCF, is obtained as

VCF=4π0π2vCtsinwt dwt   												(6.15)

The equivalent TCSC reactance is computed as the ratio of VCF to Im :

XTCSC=VCFIm=XC−XC2XC−XL2β+sin2βπ +4XC2XC−XLcos2βϖ2−1ϖtanϖβ−tanβπ (6.16)

If we apply     β=π−α, in equation (6.16) the reactance of TCSC becomes as :

XTCSC=−XC+C12π−α+sin2π−α −C2cos2π−αϖtanϖπ−α−tanπ−α (6.17)

where

C1=XC+XLCπ ,C2=4XLC2XLπ ,XLC=XCXLXC−XL ,ϖ=XCXL12

From the equation (6.17) it is clear that the reactance of TCSC is dependent on the firing angle of thyristor and this reactance varies from inductive region to capacitive region between firing angle 900 to 1800 and at around 1400 there is a condition of resonance.

A MATLAB PROGRAM is written for analyzing the active and reactive power flow control by TCSC. Output of the result shows that the compensating coefficient ‘r’ is having both inductive and capacitive compensation value which varies according to the firing angle. From the analysis it is clear that height of load angle curve increases with the more capacitive reactance of TCSC. But the height of the load angle curve decrease with more inductive reactance of TCSC.

Similarly the reactive power curve for capacitive compensation is positive and reactive power curve for inductive compensation is negative.

Also both active and reactive power decreases with the increase of firing angle up to certain value where the reactance of TCSC is inductive. At 900 of firing angle the reactance of TCSC becomes capacitive and both active and reactive power increases.

MATLAB PROGRAM-4.1

%ANALYSIS OF ACTIVE AND REACTIVE POWER FLOW

%WITH VARIATION OF FIRING ANGLE

(Attached in Appendix-‘A’)

SET OF DATA

line voltage= 220 V

line reactance= 200 ohm

inductive reactance of TCR= 0.15 ohm

fixed capacitive impedance= 130 ohm

phase angle= 300

RESULT IS

alpha        Pc              Qc            r

0        120.9092   -0.0486   -0.0008 (inductive compensation)

10.0000  120.8836   -0.0623   -0.0010  (inductive compensation)

20.0000  120.8416   -0.0848   -0.0013 (inductive compensation)

30.0000  120.7677   -0.1243   -0.0019 (inductive compensation)

40.0000  120.6245   -0.2006   -0.0031 (inductive compensation)

50.0000  120.3050   -0.3703   -0.0058 (inductive compensation)

60.0000  119.4153   -0.8381   -0.0133 (inductive compensation)

70.0000  115.7277   -2.7023   -0.0456 (inductive compensation)

80.0000   71.6491   -15.6604   -0.6888 (inductive compensation)

90.0000  345.7143  344.0686   0.6500 (capacitive compensation)

Fig-6.4

6.6	SIMULATION OF TCSC CIRCUIT USING PSCAD-4.0 :

The basic model of the TCSC is implemented in PSCAD in order to identify its main characteristics [7][23]. For the purpose of the simulation, a constant AC voltage source

Vs  = 1 kV is used to supply a series R-L load. The thyristors are fired at an angle of 130 degree. The waveforms of the simulated TCSC model are obtained for each element used in the circuit. Of course with the help of slider used for varying the firing angle, we can vary the firing angle from 900 to 1800 and there will be change in waveform.

C = Fixed Capacitor = 212 micro farad

L =Inductance used in series with thyristor = 0.015 Henry

RL= Load resistance = 1 ohm

LL = Load inductance = 1 Henry

Vcap= Voltage across fixed capacitor

Vind = Voltage across series inductor used with thyristor

Vload = Voltage across load

Icap = Current through Capacitor

Iind = Current through series inductor

Iload = Current through load

Alpha = Firing angle = 1300

Fig- 6.5

TCSC CHARACTERISTICS WAVEFORMS FOR FIRING ANGLE = 1300

Time is sec

Fig-6.6

6.7	TCSC STEADY STATE CHARACTERISTICS

(SIMULINK BLOCK)[7]:

In this circuit TCSC is used in parallel with two transmission line having inductance of  0.07956 H and fixed capacitor is having value of 176.83 micro farad. Voltage source applied is 11 kV. For the circuit steady state rms load current Iload is found.

Fig-6.7

Time in sec

Fig-6.8

From the above graph which is obtained after simulation , the Iload rms current = 1.528 kA. This load current also obtained from the RMS load current meter.

6.8	Dynamic Characteristics of TCSC :

(open loop control)

In this case the test system comprises of a constant AC voltage source feeding a linear

Series R-L load through three parallel branch transmission circuits. The equivalent impedance of each transmission path is adjusted to be equal, with one of them including a TCSC. The top branch contains a breaker, Brk, which is used to simulate the opening of this branch at a given point in time of  the transient simulation and to analyze the dynamic performance of the TCSC under the new operating condition. When Brk opens the equivalent impedance of the transmission system increases and consequently the current supplied to the load drops. The TCSC is operated at firing angle of 1300 and Brk opens at t = 0.2 secs and the dynamic characteristics of the TCSC is observed from the output graph which is obtained after simulation of the test circuit as given in Fig 6.9 in the next page.

SIMULINK BLOCK FOR TCSC OPEN LOOP CONTROL

Fig-6.9

SIMULATION RESULT :

Time is sec

Fig-6.10

From the simulation result, it is clear that the rms load current is decreased from 1.528 kA (steady state value) to 1.385 kA (when breaker opens at t = 0.2 sec). Graphical result also shows the same as Iload rms value decreases at t = 0.2 sec.

6.9	SIMULINK BLOCK FOR TCSC CLOSED LOOP CONTROL :

Fig-6.11

SIMULATION RESULT FOR TCSC CLOSED LOOP CONTROL :

Time is sec

Fig-6.12

From the result it is clear that the load current Iload (rms) which is decreased to 1.385 kA in the open loop control arrangement is automatically regain to its steady state value (1.53 kA). Thus TCSC  provides required series compensation to regain the decreased current to steady state value though one of the parallel inductor is in open condition.

From the analysis, we come to know that TCSC is good current  controller. Thus it can  be utilized as active power controller. This will be discussed in the next simulation block.

6.10	POWER FLOW CONTROL USING TCSC

(SIMULINK BLOCK)

Fig-6.13

In the above block, a two bus system is considered for simulation and analyzing the power flow control. For the above block in Fig-6.13, set of data are given in the next page and simulation result is shown.

Firing angle for thyristor = alpha =1300

Sending end voltage (line-line) = 11 kV

Receiving end voltage (line-line) = 10 kV

Sending end phase angle = 300

Receiving end phase angle = 00

Isr = Sending end current

Psr = Active power flow from sending end

Qsr = Reactive power flow from receiving end

Transmission line inductance = 0.45 H (per phase)

Fixed capacitor of TCSC = 212 micro farad

Series inductance of TCSC = 0.015 H

CASE-1                            SIMULATION RESULT  FOR FIRING ANGLE = 1300

CASE-2                            SIMULATION RESULT  FOR FIRING ANGLE = 1500

CASE-3                            SIMULATION RESULT  FOR FIRING ANGLE = 1100

Fig-6.14

From the three cases of simulation result, it is clear that as we increase the firing angle from 1300 to 1500, the TCSC causes capacitive compensation and the real power flow from sending end is increased from 988.72 KW to 1270.54 KW. Similarly when firing angle decreases from 1300 to 1100, TCSC increases the inductive reactance of the transmission line. Thus real power flow from sending end to receiving end is decreased from 988.72 KW to 538.39 KW.

6.11	CONCLUSION :

Thus with the discussion  and simulation result it is very clear that, both current and the power flow in the transmission line can be controlled by varying the firing angle of TCSC to the desired value. Now in the next two chapter, we will consider the 5-bus network and we will find the power flow between two buses using load flow solution. Also we will find out the desired amount of power flow to be controlled between two particular bus. For the analysis and result we will use MATLAB code.

7

POWER FLOW SOLUTION OF LARGE ELECTRICAL NETWORK

7.1	OBJECTIVE :

The main objective of a power flow study is to determine the steady state operating condition of the electrical power network. The steady state may be determined by finding out the flow of active and reactive power throughout the network and the voltage magnitude and phase angles at all nodes of the network [4][8].

The planning and daily operation of modern power systems call for numerous power flow studies. Such information is used to carry out security assessment analysis, where the nodal voltage magnitudes and active and reactive power flows in transmission lines and transformers are carefully observed to assess whether or not they are within prescribed operating limits. If the power flow study indicates that there are voltage magnitudes outside bounds at certain points in the  network, then appropriate control actions become necessary in order to regulate the voltage magnitude. Similarly, if the study predicts that the power flow in a given transmission line is beyond the power carrying capacity of the line then control action will be taken.

7.2	POWER FLOW SOLUTION :

A electrical network consists of various electrical elements such as generator, load, transmission line, transformer etc. Here we assume that all the data for generator, load, and transmission line parameters are given in per unit system and common MVA base [8].

Before building the power flow equation it is necessary to know the bus admittance matrix  for the given network.  Here we will build a bus admittance matrix for n-bus electrical network. The same principle can be applied to any number of buses.

7.3	BUS ADMITTANCE MATRIX :

k

Ik

Ek

m

Im

Em

R + j X

G/2 + j B/2

G/2 + j B/2

Fig 7.1

The Fig 7.1 shows a  simple transmission line connected between k-th and

m-th node and the transmission line parameter are as follows :

R = resistance of transmission line

X = reactance of transmission line

G = conductance of transmission line

B = susceptance of transmission line

Ik = current injected at the k-th node

Im = current injected at m-th node

Ek = voltage at k-th node

Em = voltage at m-th node

Self admittance at node-k is given by

ykk=1R+jX+G2+jB2=RR2+X2+G2−jXR2+X2+jB2			(7.1)

ykm=−1R+jX=−RR2+X2+jXR2+X2						(7.2)

ykm=−ymk

Also shunt element connected each node contributes to Ybus matrix. The additional amount of self admittance is added to ykk. The contribution of shunt element to Ybus admittance matrix is given by :

ykk(shunt)=1Rsh+jXsh=RshR2sh+X2sh−jXshR2sh+X2sh				(7.3)

where as ykk is called self-admittance and these elements constitute diagonal element of Ybus matrix and ykm, ymk is called mutual admittance and these elements constitute the off-diagonal element of the Ybus matrix. In general Ybus matrix for a n-bus network can be written as :

Ybus=Y11 Y12 ⋯⋯Y1nY21 Y22⋯⋯Y2n⋮ ⋮ ⋮ 							(7.4)

7.4	POWER FLOW EQUATION [8] :

In order to develop suitable power flow equations, it is necessary to find relationship between injected bus currents and bus voltages. Based on above fig 7.1 the injected complex current at bus-k which is denoted by Ik may be expressed in terms of complex bus voltage Ek and Em as follows :

Ik=yk0Ek+ykmEk−Em=yk0+ykmEk−ykmEm=YkkEk+YkmEm		(7.5)

where Ykk=yko+ykm and Ykm=−ykm

Similarly for bus m,

Im=ymoEm+ymkEm−Ek=ym0+ymkEm−ymkEk=YmmEm+YmkEk		(7.6)

where Ymm=ymo+ymk and Ymk=−ykm

The above equation can be written in matrix form as :

Ik 								(7.7)

where the bus admittances and voltage can be expressed in more explicit form:

Yij=Gij+jBij

Ei=Viejθi=Vicosθi+jsinθi

where i = k,m and j = k,m

The Complex power injected at bus k  is given by :

Sk=Pk+jQk=EkIkEkYkkEK+YkmEm

where Ik* is the complex conjugate of the current injected at bus k

Applying the value of Yij and Ei in Sk we get,

Sk=Vkcosθk+jsinθkGkk+jBkkVkcosθk+jsinθk+Gkm+jBkmVmcosθm+jsinθm

The expression for real and reactive power injected at k-th bus can be determined by taking real and imaginary parts of the above expression of Sk.

So the real power injected at k-th bus is

Pkcal=Vk2Gkk+VkVm[Gkmcosθk−θm+Bkmsinθk−θm]				(7.8)

Similarly the reactive power injected at k-th bus is

Qkcal=−Vk2Bkk+VkVm[Gkmsinθk−θm−Bkmcosθk−θm]			(7.9)

From the equations (7.8) and (7.9) it is clear that the powers injected at bus k is flown through the ith element of the transmission line. However, a practical power system will consists of many buses and many transmission line elements. This calls for the above two equation to be expressed as the summation of the power flowing at each one of the transmission elements terminating at this bus. This is illustrated in Fig 7.2 and  Fig 7.3 for the cases of active and reactive powers respectively .

m

PLk

PGk

Pkn cal

k     Pki cal

Pkl cal

Active power balance at bus k

Fig-7.2

m

QLk

QGk

Qkn cal

k     Qki cal

Qkl cal

Reactive power balance at bus k

Fig-7.3

The generic net active and reactive powers injected at bus k are:

Pkcal=i=1nPkical

Qkcal=i=1nQkical

where Pkical and Qkical are active and reactive power flows contributed  by the mutual admittance elements i.e  from k-bus to m-bus.

7.5	POWER MISMATCH EQUATIONS [4][8] :

For steady state operation of power system, at a given bus the generation, load and power exchanged through the transmission elements connecting to the bus must add up to zero. This applies to both active and reactive power. These equations are termed as ‘power mismatch equations’ and at bus k they take the following form :

ΔPk=PGk−PLk−Pkcal=Pksch−Pkcal=0

ΔQk=QGk−QLk−Qkcal=Qksch−Qkcal=0

where the terms ΔPk and ΔQk are the mismatch active and reactive powers at bus k respectively.

PGk and QGk represents the active and reactive powers injected by the generator at bus k respectively.

PLk and QLk represents the active and reactive powers drawn by the load at bus-k respectively.

Further for specified levels of power generation and power load at bus k  the power mismatch equations can be written as :

ΔPk=PGk−PLk−Vk2Gkk+VkVm[Gkmcosθk−θm+Bkmsinθk−θm]=0 	(7.10)

ΔQk=QGk−QLk−−Vk2Bkk+VkVm[Gkmsinθk−θm−Bkmcosθk−θm]=0 	(7.11)

The generic power mismatch equations at bus k are :

ΔPk=PGk−PLk−i=1nPki cal=0 							(7.12)

ΔQk=QGk−QLk−i=1nQkical=0 							(7.13)

7.6	NET ACTIVE AND REACTIVE POWER:

The generation and the load at bus k may be measured by the electric utility and in the parlance of power system engineers, their net values are known as the ‘scheduled active and reactive powers’ :

Pksch=PGk−PLk

Qksch=QGk−QLk

7.7	VARIABLES AND BUS TYPE :

Four variables are associated with each bus. These are [7]

voltage magnitude V

phase angle θ

real power P

reactive power Q

The system buses are generally classified into three types and these are :

Slack Bus : 	It is the reference bus, where the magnitude and phase angle of the voltage are specified. This bus makes up the difference between the scheduled loads and generated power that are caused by the losses in the network.

Load Bus : 	At these buses the active and reactive powers are specified. The magnitude and phase angle of the voltage are unknown. These buses are called P-Q buses.

Regulated buses : 	These buses are the generator buses. These are also known as voltage controlled buses. At these buses, the real power and voltage magnitude are specified. The phase angle of the voltages and the reactive power are to be determined. The limits on the value of the reactive power are also specified. These buses are called

P-V buses.

7.8	POWER FLOW SOLUTION METHOD :

The most common techniques used for the iterative solution of nonlinear algebra equations are Gauss-Seidel, Newton-Raphson method etc [4]. As power flow equation are nonlinear in nature, the following three common methods used for the solution of power flow equation.

(a) Gauss-Seidel (GS) method

(b) Newton-Raphson (NR) method

(c) Fast Decoupled power flow solution method

Out of these three method, use of Newton-Raphson (NR) method is more powerful for medium and large network. This is because it works faster and is sure to converge in most cases. Number of iteration  required is less and the convergence process is faster than any other method. Its only draw back is the large requirement of computer memory, which can be overcome through a compact storage scheme.  That’s why in this project Newton-Raphson method  is used to solve power flow equation.

7.9	Newton-Raphson Algorithm :

This approach uses iteration to solve the following set of nonlinear algebraic equations [7][8] :

f1=x1,x2,⋯,xn=0f2=x1,x2,⋯,xn=0⋮ ⋮ ⋮fN=x1,x2,⋯,xn=0

Or FX=0 								 	(7.14)

where F represents the set of n nonlinear equations and X is the vector of n unknown state variables.

The essence of the method consists of determining the vector of state variables X by performing a Taylor series expansion of F(x) about an initial estimate X(0) :

FX=FX0+JX0X−X0+higher−order terms			(7.15)

where JX0 is a matrix of first-order partial derivatives of F(X) with respect to X and is called Jacobian which is evaluated at X=X(0).

This expansion in equation (7.15) lends itself to a suitable formulation for calculating the vector of state variables X by assuming that X(1) is the value computed by the algorithm at iteration 1 and that this value is sufficiently close to the initial estimate X(0). Based on this premise, all high-order derivatives terms in the expression. (5.15) can be neglected. Hence,

f1X1f2X1 ⋮

FX1       FX0    JX0  X1−X0

In compact form, and generalizing the above expression for the case of

iteration ( i ),

FXi≈FXi−1+JXi−1Xi−Xi−1 					(7.16)

Where i = 1, 2 …….Furthermore, if it is assumed that X(i) is sufficiently close to the solution X(*)

Then FX(i)≈FX=0

Hence the equation (7.16) can be written as

FXi−1+JXi−1Xi−Xi−1=0						(7.17)

Now solving the equation (7.17) for X(i),

Xi=Xi−1−J−1Xi−1FXi−1  						(7.18)

The iterative solution can be expressed as a function of the correction vector

ΔXi=Xi−Xi−1,

ΔXi=−J−1Xi−1FXi−1   						(7.19)

and the initial estimates are updated using the following relations:

Xi=Xi−1+ΔXi   								(7.20)

The calculation is repeated as many times as required using the most up-to-date values of X in the above equation. This is done until mismatches ΔX are within a prescribed small tolerance (i.e 1e-12).

7.10	NEWTON-RAPHSON METHOD FOR POWER FLOW  PROBLEM :

Similar analogy can be made for power flow equation as described above as the power flow equation is also a nonlinear algebraic equation consists of variables nodal voltage magnitudes V and phase angles θ. Thus the power mismatches equations ΔPand ΔQare expanded around a base point θ0,V0 and hence, the power flow Newton-Raphson algorithm is expressed by the following relationship [8] :

ΔP 						  (7.21)

Further this can be written in this form as:

ΔP  							  (7.22)

where J1, J2, J3 and J4 constitutes the Jacobian matrix,  each element  of the order of

(nb-1) x (nb-1).

nb= total number of buses

Thus Jacobian matrix are written as :

J1=∂Pk∂θm ,    J2=∂Pk∂VmVm

J3=∂Qk∂θm,     J4=∂Qk∂VmVm

where k = 1,2, ……,nb

and m = 1,2, ………,nb

but omitting the slack bus entries.

It must be pointed out that the correction terms ΔVm are divided by Vm to compensate for the fact that Jacobian terms ∂Pk∂VmVm and ∂Qk∂VmVm are multiplied by Vm. It is shown in the derivative terms given below that this artifice yields useful simplifying calculations.

Consider the l-th elements connected between buses k and m  in Fig.7.1 for which self and mutual Jacobian terms are given below:

For k≠m:

∂Pk,l∂θm,l=VkVm[Gkmsinθk−θm−Bkmcosθk−θm] 		(7.23)

∂Pk,l∂Vm,lVm,l=VkVm[Gkmcosθk−θm+Bkmsinθk−θm] 	(7.24)

∂Qk,l∂θm,l=−∂Pk,l∂Vm,lVm,l  							(7.25)

∂Qk,l∂Vm,lVm,l=∂Pk,l∂Vm,l 							(7.26)

For k=m

∂Pk,l∂θk,l=−Qkcal−Vk2Bkk 						(7.27)

∂Pk,l∂Vk,lVk,l=Pkcal+Vk2Gkk 						(7.28)

∂Qk,l∂θk,l=Pkcal−Vk2Gkk  						(7.29)

∂Qk,l∂Vk,lVk,l=Qkcal−Vk2Bkk 						(7.30)

In general, for a bus k containing n transmission elements l, the bus self-elements take the following form :

∂Pk∂θk=l=1n∂Pk,l∂θk,l 							(7.31)

∂Pk∂VkVk=l=1n∂Pk,l∂Vk,lVk,l 							(7.32)

∂Qk∂θk=l=1n∂Qk,l∂θk,l 							(7.33)

∂Qk∂VkVk=l=1n∂Qk,l∂Vk,lVk,l 						(7.34)

After the convergence of the power flow solution, we get the final value of state variables i.e. voltage magnitudes and phase angles have been calculated. Then active and reactive power flows throughout the transmission system are determined quite straightforwardly.

7.11	STATE VARIABLE INITIALISATION :

The effectiveness of the Newton-Raphson method to achieve feasible iterative solutions is dependent upon the selection of suitable initial values for all the state variables involved in the study [8].

The power flow solution starts with initial value of voltage magnitude of 1 p.u. at all PQ buses. The slack and PV buses are given their specified values, which remain constant throughout the iterative solution if no generator reactive power limits are violated. The initial voltage phase angles are selected to be 0 at all buses.

7.12	GENERATOR REACTIVE POWER LIMIT :

For the iterative solution of power flow equation, it is essential to check the calculated reactive power Qkcal is within the generator reactive power limits [8] :

QG min k <QGk<QG max k

If either of the following conditions occur during the iterative  process :

Qkcal≥QG max k ,

Qkcal≤QG min k ,

Bus k becomes a generator PQ bus with either of the following mismatch power equations incorporated in Power flow mismatch equation as:

ΔQk=Qk=QG max k−QLk−Qkcal,ΔQk=Qk=QG min k−QLk−Qkcal,

Depending on the violated limit, together with relevant Jacobian entries. The nodal voltage magnitude at bus k is allowed to vary and Vk becomes a state variable.

It should be remarked that bus k may revert to being a generator PV bus at some point

during the iterative process if better estimates of Qkal, calculated with more accurate nodal voltages, indicate that the reactive power requirements at bus k can, after all be met by the generator connected at bus k. Hence, reactive power limit checking is carried out  at  each iteration.

7.13	GENERALIZED POWER FLOW SOLUTION FOR

5-BUS NETWORK:

A 5-Bus network is given in the next page in Fig-7.4 to analyze the power flow solution and to determine the active power flow and reactive power flow from each bus . Also nodal voltage magnitude and nodal phase angle is determined where these quantities are not known. For this purpose a computer program is used to solve the power flow solution.

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

Tline-1

Tline-7

Tline-2

Tline-6

Tline-5

Tline-3

Tline-4

Gen-2

Gen-1

LOAD-1

LOAD-2

LOAD-4

LOAD-3

Fig 7.4     A 5-Bus Network for analyzing the power flow  solution

DATA FOR 5-BUS NETWORK :

TRANSMISSION LINE DATA :

Total no of transmission line = 7

| Transmission Line | Fm | To | Resistance in p.u | Reactance in p.u | Susceptance in p.u |
| --- | --- | --- | --- | --- | --- |
| Tline-1 | Delhi | Noida | 0.02 | 0.06 | 0.06 |
| Tline-2 | Delhi | Najafgarh | 0.08 | 0.24 | 0.05 |
| Tline-3 | Noida | Najafgarh | 0.06 | 0.18 | 0.04 |
| Tline-4 | Noida | Faridabad | 0.06 | 0.18 | 0.04 |
| Tline-5 | Noida | Gurgaon | 0.04 | 0.12 | 0.03 |
| Tline-6 | Najafgarh | Faridabad | 0.01 | 0.03 | 0.02 |
| Tline-7 | Faridabad | Gurgaon | 0.08 | 0.24 | 0.05 |

GENERATOR BUS DATA

Total no of Generator = 2

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power injected in p.u | Reactive power injected in p.u | Generators reactive power upper limits in p.u | Generators reactive power lower limit in p.u |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Delhi-1 | Slack Bus | 1.06 | 0 | unknown | unknown | 5 | -5 |
| Noida-2 | Generator PV Bus | 1.00 | ? | 0.4 | ? | 3 | -3 |

LOAD BUS DATA

Total no of load = 4

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power drawn in p.u | Reactive power drawn in p.u |
| --- | --- | --- | --- | --- | --- |
| Noida-2 | Load PQ Bus | ? | ? | 0.20 | 0.10 |
| Najafgarh-3 | Load PQ Bus | ? | ? | 0.45 | 0.15 |
| Faridabad-4 | Load PQ Bus | ? | ? | 0.40 | 0.05 |
| Gurgaon-5 | Load PQ Bus | ? | ? | 0.60 | 0.1 |

General Parameters :

Maximum Iteration = 100,

Tolerance = 1e – 12

MATLAB PROGRAM-5.1

COMPUTER PROGRAM FOR POWER FLOW SOLUTION

USING NEWTON-RAPHSON METHOD :

For the 5-bus network shown in Fig 5.4, a computer program is written using MATLAB code to solve the power flow equation. These program are attached in Appendix-‘B’ . Here the main program is shown .

% Main Program to get the output of power flow solution of a given network

%BUS DATA

% nb = number of buses

% bus type = type of bus

% VM = nodal voltage magnitude

% VA = nodal voltage phase angle

% TYPE OF BUS USED IN THE NETWORK

% bus type = 1 is slack or swing bus

% bus type = 2 is generator PV bus

% bus type = 3 is load PQ bus

% bus type = 4 is generator bus

% The five buses in the network are numbered for the purpose of the power

% flow solution, as follows :

% DELHI = 1

% NOIDA = 2

% NAJAFGARH = 3

% FARIDABAD = 4

% GURGAON = 5

nb=5;

bus type(1)=1; VM(1)=1.06; VA(1)=0;

bus type(2)=2; VM(2)=1;    VA(2)=0;

bus type(3)=3; VM(3)=1;    VA(3)=0;

bus type(4)=3; VM(4)=1;    VA(4)=0;

bus type(5)=3; VM(5)=1;    VA(5)=0;

%GENERATOR DATA

% ngn = number of generators

% genbus = generator bus number

% PGEN = scheduled active power contributed by the generator

% QGEN = scheduled reactive power contributed by the generator

% QMAX = generator reactive power upper limit

% QMIN = generator reactive power lower limit

ngn=2;

genbus(1)=1; PGEN(1)=0;   QGEN(1)=0; QMAX(1)=5; QMIN(1)=-5;

genbus(2)=2; PGEN(2)=0.4; QGEN(2)=0; QMAX(2)=3; QMIN(2)=-3;

%TRANSMISSION LINE DATA

% ntl = number of transmission lines

% tlsend = sending end of transmission line

% tlrec = receiving end of transmission line

% tlresis = series resistance of transmission line

% tlreac = series reactance of transmission line

% tlcond = shunt conductance of transmission line

% tlsuscep = shunt susceptance of transmission line

ntl=7;

tlsend(1)=1; tlrec(1)=2; tlresis(1)=0.02; tlreac(1)=0.06; tlcond(1)=0; tlsuscep(1)=0.06;

tlsend(2)=1; tlrec(2)=3; tlresis(2)=0.08; tlreac(2)=0.24; tlcond(2)=0; tlsuscep(2)=0.05;

tlsend(3)=2; tlrec(3)=3; tlresis(3)=0.06; tlreac(3)=0.18; tlcond(3)=0; tlsuscep(3)=0.04;

tlsend(4)=2; tlrec(4)=4; tlresis(4)=0.06; tlreac(4)=0.18; tlcond(4)=0; tlsuscep(4)=0.04;

tlsend(5)=2; tlrec(5)=5; tlresis(5)=0.04; tlreac(5)=0.12; tlcond(5)=0; tlsuscep(5)=0.03;

tlsend(6)=3; tlrec(6)=4; tlresis(6)=0.01; tlreac(6)=0.03; tlcond(6)=0; tlsuscep(6)=0.02;

tlsend(7)=4; tlrec(7)=5; tlresis(7)=0.08; tlreac(7)=0.24; tlcond(7)=0; tlsuscep(7)=0.05;

% SHUNT DATA

% nsh = number of shunt elements

% shbus = shunt element bus number

% shresis = resistance of shunt element

% shrea = reactance of shunt element

% +ve for inductive reactance and -ve for capacitive reactance

nsh=0;

shbus(1)=0; shresis(1)=0; shreac(1)=0;

%LOAD DATA

% nld = number of load elements

% loadbus = load element bus number

% PLOAD = scheduled active power consumed at the bus

% QLOAD = scheduled reactive power consumed at the bus

nld=4;

loadbus(1)=2; PLOAD(1)=0.2;  QLOAD(1)=0.1;

loadbus(2)=3; PLOAD(2)=0.45; QLOAD(2)=0.15;

loadbus(3)=4; PLOAD(3)=0.4;  QLOAD(3)=0.05;

loadbus(4)=5; PLOAD(4)=0.6;  QLOAD(4)=0.1;

% GENERAL PARAMETERS

% itmax = maximum number of iterations permitted before the iterative

% process is terminated

% tol= criterion tolerance to be met before the iterative solution is

% successfully brought to an end

itmax=100;

tol=1e-12;

nmax=2*nb;

VA=VA*180/pi;

MVAbase=100; % base MVA

[YR,YI]=Ybus(tlsend,tlrec,tlresis,tlreac,tlsuscep,tlcond,shbus,shresis,shreac,ntl,nb,nsh);

[VM,VA,it]=NewtonRaphson(nmax,tol,itmax,ngn,nld,nb,bustype,genbus,loadbus,PGEN,QGEN,QMAX,QMIN,PLOAD,QLOAD,YR,YI,VM,VA);

[PQsend,PQrec,PQloss,PQbus]=PQflows(nb,ngn,ntl,nld,genbus,loadbus,tlsend,tlrec,tlresis,tlreac,

tlcond,tlsuscep,PLOAD,QLOAD,VM,VA);

Psend=real(PQsend)*MVAbase; % active power sent from each bus

Qsend=imag(PQsend)*MVAbase; % reactive power sent from each bus

Prec=real(PQrec)*MVAbase; % active power received at each bus

Qrec=imag(PQrec)*MVAbase; % reactive power received at each bus

Ploss=real(PQloss)*MVAbase; % active power loss in each transmission line

Qloss=imag(PQloss)*MVAbase; % reactive power loss in each transmission line

Pinjected=(real(PQbus)*MVAbase);

Pgen=[Pinjected(1,1) Pinjected(1,2) -PLOAD(1)*MVAbase Pinjected(1,3) Pinjected(1,4) Pinjected(1,5)];

Qinjected=(imag(PQbus)*MVAbase);

Qgen=[Qinjected(1,1) Qinjected(1,2) -QLOAD(1)*MVAbase Qinjected(1,3) Qinjected(1,4) Qinjected(1,5)];

disp ('ACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI      DELHI    NOIDA      NOIDA    NOIDA         NAJAF    FBAD')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD     GURGAON')

disp ('    =====     =====      =====      ====       =======       =======  ======== ')

disp(Psend)

disp ('ACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====      =====      =====       ====         =======      =======   ========')

disp(Prec)

disp ('ACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI      DELHI     NOIDA      NOIDA    NOIDA           NAJAF     FBAD')

disp ('    NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD       GURGAON')

disp ('    =====        =====    =====         ====       =======       =======   ========')

disp(Ploss)

disp ('REACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI      DELHI    NOIDA      NOIDA    NOIDA           NAJAF     FBAD')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON     FBAD       GURGAON')

disp ('    =====       =====     =====        ====       =======       =======   ========')

disp(Qsend)

disp ('REACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====       =====   =====         ====       =======        =======   ========')

disp(Qrec)

disp ('REACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI      DELHI     NOIDA      NOIDA    NOIDA           NAJAF     FBAD')

disp ('    NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD       GURGAON')

disp ('    =====       =====     =====        ====         =======       =======   ========')

disp(Qloss)

disp ('NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   ')

disp(Pgen)

disp (' NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   ')

disp(Qgen)

TOTALGEN =(PQbus(1,1)+PQbus(1,2))*MVAbase;

TOTALGENERATION_ACTIVEPOWER =real(TOTALGEN)

TOTALGENERATION_REACTIVEPOWER =imag(TOTALGEN)

TOTAL_ACTIVE_LOAD=-(PLOAD(1)+PLOAD(2)+PLOAD(3)+PLOAD(4))*MVAbase

TOTAL_REACTIVE_LOAD=-(QLOAD(1)+QLOAD(2)+QLOAD(3)+QLOAD(4))*MVAbase

TOTAL_ACTIVEPOWER_LOSS=TOTALGENERATION_ACTIVEPOWER + TOTAL_ACTIVE_LOAD

TOTAL_REACTIVEPOWER_LOSS=TOTALGENERATION_REACTIVEPOWER + TOTAL_REACTIVE_LOAD

TOTAL_ITERATION = it

% end of main program

EXECUTION OF MAIN PROGRAM :

When this main program is executed the list of result is obtained which is summarized as below in the next page.

SUMMARY OF OUTPUTS :

ACTIVE POWER SENT FROM EACH BUS::::

DELHI       DELHI   NOIDA      NOIDA    NOIDA          NAJAF    FBAD

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====   =====        ====       =======       =======  ========

89.4458      42.0023   24.5614     27.8124    54.7540          19.3916     6.6320

ACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====    =====       ====       =======       =======   ========

-86.8455     -40.2730   -24.1132   -27.2521  -53.4448        -19.3461     -6.5552

ACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI       DELHI   NOIDA      NOIDA    NOIDA          NAJAF     FBAD

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====   =====        ====       =======       =======   ========

2.6002        1.7293    0.4482       0.5603      1.3092            0.0455       0.0768

REACTIVE POWER SENT FROM EACH BUS::::

DELHI       DELHI   NOIDA      NOIDA    NOIDA          NAJAF    FBAD

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====   =====        ====        =======      =======   ========

74.1880       17.0217  -2.4910      -1.6897    5.6034            2.8679        0.5491

REACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF    NAJAF       FBAD     GURGAON    FBAD      GURGAON

=====        =====     =====         ====      =======       =======   ========

-72.9084      -17.5125  -0.3523      -0.8306       -4.8292         -4.6878      -5.1708

REACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI       DELHI   NOIDA      NOIDA    NOIDA          NAJAF     FBAD

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====         =====   =====       ====        =======      =======   ========

1.2797       -0.4908   -2.8433      -2.5202      0.7742         -1.8199        -4.6216

NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::

DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON

131.4481    40.2823   -20.0000     -44.9946   -39.9663    -60.0000

NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS:

DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON

91.2097    -61.4856   -10.0000    -14.9969     -4.9692    -10.0000

TOTAL GENERATION_ACTIVE POWER =

171.7304

TOTAL GENERATION_REACTIVE POWER =

29.7241

TOTAL_ACTIVE_LOAD =

-165

TOTAL_REACTIVE_LOAD =

-40

TOTAL_ACTIVE POWER_LOSS =

6.7304

TOTAL_REACTIVE POWER_LOSS =

-10.2759

TOTAL  ITERATION =

6

7.14	CONCLUSION:

The summary of result are superimposed on the given 5-bus network shown in Fig-5.5, so that at each bus we can find out how much power flows from each bus and the losses on the transmission line are also mentioned. The summary of output shows that at each bus, power mismatch equation is satisfied. Also power flow solution is converges to a prescribed tolerance of 1e-12 within six iteration.

86.84

72.90

40.28        61.48

Gen-2

Gen-1

131.44              91.20

24.11

0.35

27.81

1.68

19.34

4.68

19.39

2.86

53.44

4.82

27.25

0.83

24.56

2.49

54.75

5.60

40.27

17.51

42.00

17.02

6.55

5.17

6.63

0.54

88.44

74.18

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

60 + j10

40 + j5

20 +j10

Fig-7.5

Active and Reactive power flow shown at each bus for 5-bus network.

Active Power

45 + j15

Reactive Power

8

POWER FLOW CONTROL USING TCSC

8.1	ACTIVE AND REACTIVE POWER FLOW THROUGH TCSC :

As Thyristor Controlled Series Capacitor (TCSC) will control  the power flow in the transmission line of a large electrical network, here we will model the TCSC as a variable reactance which varies in terms of firing angle of thyristor [7][8][13].

XC

m

Im

Vm

k

Ik

Vk

XL

Fig-6.1

TCSC connected between to buses k and m

The fundamental frequency equivalent reactance XTCSC of the TCSC  which is already derived in equation (6.17) is given by :

XTCSC=−XC+C12π−α+sin2π−α−C2cos2π−αϖtanϖπ−α−tanπ−α

where

C1=XC+XLCπ ,C2=4XLC2XLπ ,XLC=XCXLXC−XL ,ϖ=XCXL12

The TCSC active and reactive power equations at bus k are

Pk=VkVmBkmsinθk−θm, (8.1)Qk=−Vk2Bkk−VkVmBkmcosθk−θm (8.2)

where

Bkk=−Bkm=BTCSC=1XTCSC

Similarly  the active and reactive power equations at bus m are :

Pm=VmVkBmksinθm−θk, (8.3)Qm=−Vm2Bmm−VmVkBmkcosθm−θk (8.4)

where

Bmm=−Bmk=BTCSC=1XTCSC

For the case when the TCSC controls active power flowing from bus k to bus m at a specified value, the set of linearised power flow equations is :

ΔPkΔPmΔQkΔQm     (8.5)

where ΔP, ΔQ, ΔPkmαTCSC constitute ‘power mismatch equation’ and these are expressed as:

ΔPk=PGk−PLk−Pkcal=Pksch−Pkcal=0

ΔQk=QGk−QLk−Qkcal=Qksch−Qkcal=0

ΔPkmαTCSC=Pkmreg−PkmαTCSC,cal

where

Pkmreg= The active power to be controlled from bus k to bus m

PkmαTCSC,cal = calculated active power of the TCSC at bus k

Similarly  Δθ, ΔV, ΔαTCSC constitute state variables and expressed as :

Δθ=θi+1−θi

ΔV=Vi+1−Vi

ΔαTCSC=αTCSC (i+1)−αTCSC (i)

ΔαTCSC is the incremental change in the TCSC firing angle at the ith iteration.

The Jacobian elements for the series reactance, as a function of the firing angle αTCSC are given below [8] :

Partial derivatives of the variable series impedance model are :

∂Pk∂XX=−VkVmBkmsin(θk−θm)							  (8.6)

∂Qk∂XX=Vk2Bkk+VkVmBkmcos(θk−θm)						   (8.7)

∂Pkm∂XX=∂Pk∂XX									(8.8)

Partial derivatives of the firing angle model is given by :

∂Pk∂α=PkBTCSC∂XTCSC∂α								(8.9)

∂Qk∂α=QkBTCSC∂XTCSC∂α								(8.10)

∂BTCSC∂α=BTCSC2∂XTCSC∂α								(8.11)

∂XTCSC∂α=−2C11+cos2α+C2sin2αϖtanϖπ−α−tanα +C2ϖ2cos2π−αcos2ϖπ−α−1 (8.12)

8.2	POWER FLOW SOLUTION FOR 6-BUS NETWORK:

Power flow solution for the network where TCSC is used in the network is solved in the similar way using Newton-Raphson method already discussed in Chapter-7. In the next page a 6-Bus network is drawn, in which a TCSC is used in between Najafgarh to Dwarka. By writing a MATLAB code in the similar fashion as written in Chapter-7 for power flow solution, we analyze how the Thyristor-Controlled Series Capacitor is effective for controlling the specified amount  of active power in between two buses.

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

Tline-1

Tline-7

Tline-2

Tline-6

Tline-5

Tline-3

Tline-4

Gen-2

Gen-1

LOAD-1

LOAD-2

LOAD-4

LOAD-3

TCSC1

DWARKA-6

Fig —8.2

6-bus network where one TCSC is introduced in between Najafgarh bus and Dwarka bus

DATA FOR 6-BUS NETWORK IN WHICH TCSC-1 IS CONNECTED :

TRANSMISSION LINE DATA :

Total no of transmission line = 7

| Transmission Line | Fm | To | Resistance in p.u | Reactance in p.u | Susceptance in p.u |
| --- | --- | --- | --- | --- | --- |
| Tline-1 | Delhi | Noida | 0.02 | 0.06 | 0.06 |
| Tline-2 | Delhi | Najafgarh | 0.08 | 0.24 | 0.05 |
| Tline-3 | Noida | Najafgarh | 0.06 | 0.18 | 0.04 |
| Tline-4 | Noida | Faridabad | 0.06 | 0.18 | 0.04 |
| Tline-5 | Noida | Gurgaon | 0.04 | 0.12 | 0.03 |
| Tline-6 | Dwarka | Faridabad | 0.01 | 0.03 | 0.02 |
| Tline-7 | Faridabad | Gurgaon | 0.08 | 0.24 | 0.05 |

GENERATOR BUS DATA

Total no of Generator = 2

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power injected in p.u | Reactive power injected in p.u | Generators reactive power upper limits in p.u | Generators reactive power lower limit in p.u |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Delhi-1 | Slack Bus | 1.06 | 0 | unknown | unknown | 5 | -5 |
| Noida-2 | Generator PV Bus | 1.00 | ? | 0.4 | ? | 3 | -3 |

LOAD BUS DATA

Total no of load = 4

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power drawn in p.u | Reactive power drawn in p.u |
| --- | --- | --- | --- | --- | --- |
| Noida-2 | Load PQ Bus | ? | ? | 0.20 | 0.10 |
| Najafgarh-3 | Load PQ Bus | ? | ? | 0.45 | 0.15 |
| Faridabad-4 | Load PQ Bus | ? | ? | 0.40 | 0.05 |
| Gurgaon-5 | Load PQ Bus | ? | ? | 0.60 | 0.1 |

TCSC’s DATA

Total no of TCSC = 1

Connected between : Najafgarh-3  to Dwarka-6

Capacitive reactance of TCSC = 9.375e-3

Inductive reactance of TCSC = 1.625e-3

Initial Firing angle = 145 degree

Firing angle lower limit = 90 degree

Firing angle upper limit = 180 degree

Active power to be controlled = 0.21 p.u

General Parameters :

Maximum Iteration = 100,

Tolerance = 1e – 12

MATLAB PROGRAM--6.1

COMPUTER PROGRAM FOR POWER FLOW CONTROL USING TCSC (THYRISTOR CONTROLLED SERIES CAPACITOR) :

To solve the power flow equation of above network which contains one TCSC to control the required amount of active power between  DWARKA and FARIDABAD, a program is written in MATLAB code  and is attached in Appendix -‘C ‘. Only the main program is shown here.

% Main  TCSC –FA Program to get the output of power flow solution of a given network

%BUS DATA

% nb = number of buses

% bustype = type of bus

% VM = nodal voltage magnitude

% VA = nodal voltage phase angle

% TYPE OF BUS USED IN THE NETWORK

% bustype = 1 is slack or swing bus

% bustype = 2 is generator PV bus

% bustype = 3 is load PQ bus

% bustype = 4 is generator bus

% The six buses in the network are numbered for the purpose of the power

% flow solution, as follows :

% DELHI = 1

% NOIDA = 2

% NAJAFGARH = 3

% FARIDABAD = 4

% GURGAON = 5

% DWARKA = 6

nb=6;

bustype(1)=1;VM(1)=1.06;VA(1)=0;

bustype(2)=2;VM(2)=1;VA(2)=0;

bustype(3)=3;VM(3)=1;VA(3)=0;

bustype(4)=3;VM(4)=1;VA(4)=0;

bustype(5)=3;VM(5)=1;VA(5)=0;

bustype(6)=3;VM(6)=1;VA(6)=0;

%GENERATOR DATA

% ngn = number of generators

% genbus = generator bus number

% PGEN = scheduled active power contributed by the generator

% QGEN = scheduled reactive power contributed by the generator

% QMAX = generator reactive power upper limit

% QMIN = generator reactive power lower limit

ngn=2;

genbus(1)=1; PGEN(1)=0;   QGEN(1)=0; QMAX(1)=5; QMIN(1)=-5;

genbus(2)=2; PGEN(2)=0.4; QGEN(2)=0; QMAX(2)=3; QMIN(2)=-3;

%TRANSMISSION LINE DATA

% ntl = number of transmission lines

% tlsend = sending end of transmission line

% tlrec = receiving end of transmission line

% tlresis = series resistance of transmission line

% tlreac = series reactance of transmission line

% tlcond = shunt conductance of transmission line

% tlsuscep = shunt susceptance of transmission line

ntl=7;

tlsend(1)=1; tlrec(1)=2; tlresis(1)=0.02; tlreac(1)=0.06; tlcond(1)=0; tlsuscep(1)=0.06;

tlsend(2)=1; tlrec(2)=3; tlresis(2)=0.08; tlreac(2)=0.24; tlcond(2)=0; tlsuscep(2)=0.05;

tlsend(3)=2; tlrec(3)=3; tlresis(3)=0.06; tlreac(3)=0.18; tlcond(3)=0; tlsuscep(3)=0.04;

tlsend(4)=2; tlrec(4)=4; tlresis(4)=0.06; tlreac(4)=0.18; tlcond(4)=0; tlsuscep(4)=0.04;

tlsend(5)=2; tlrec(5)=5; tlresis(5)=0.04; tlreac(5)=0.12; tlcond(5)=0; tlsuscep(5)=0.03;

tlsend(6)=3; tlrec(6)=4; tlresis(6)=0.01; tlreac(6)=0.03; tlcond(6)=0; tlsuscep(6)=0.02;

tlsend(7)=4; tlrec(7)=5; tlresis(7)=0.08; tlreac(7)=0.24; tlcond(7)=0; tlsuscep(7)=0.05;

% SHUNT DATA

% nsh = number of shunt elements

% shbus = shunt element bus number

% shresis = resistance of shunt element

% shrea = reactance of shunt element

% +ve for inductive reactance and -ve for capacitive reactance

nsh=0;

shbus(1)=0; shresis(1)=0; shreac(1)=0;

%LOAD DATA

% nld = number of load elements

% loadbus = load element bus number

% PLOAD = scheduled active power consumed at the bus

% QLOAD = scheduled reactive power consumed at the bus

nld=4;

loadbus(1)=2; PLOAD(1)=0.2;  QLOAD(1)=0.1;

loadbus(2)=3; PLOAD(2)=0.45; QLOAD(2)=0.15;

loadbus(3)=4; PLOAD(3)=0.4;  QLOAD(3)=0.05;

loadbus(4)=5; PLOAD(4)=0.6;  QLOAD(4)=0.1;

%TCSC DATA

% NTCSCFA = Number of TCSC

% TCSCFAsend = Sending bus

% TCSCFArec = Receiving bus

% Xc = TCSC's reactance (p.u.)

% Xl = TCSC's inductance (p.u)

% FA = Initial firing angle (deg)

% FALo = Firing angle lower limit (deg)

% FAHi = Firing angle higher limit (deg)

% Flow = Power flow direction:1 is for sending to receiving bus;

% -1 indicates opposite direction

%Psp = Active power flow to be controlled (p.u)

%PSta = Indicate the control status for active power : 1 is on; 0 is off

NTCSCFA=1;

TCSCFAsend(1)=3;TCSCFArec(1)=6;Xc(1)=9.375e-3;Xl(1)=1.625e-3;

FA(1)=145;FALo(1)=90;FAHi(1)=180;Flow(1)=1;PSta(1)=1;Psp(1)=0.21;

% GENERAL PARAMETERS

% itmax = maximum number of iterations permitted before the iterative

% process is terminated

% tol= criterion tolerance to be met before the iterative solution is

% successfully brought to an end

itmax=100;

tol=1e-12;

nmax=2*nb;

VA=VA*180/pi;

MVAbase=100; % base MVA

[YR,YI]=Ybus(tlsend,tlrec,tlresis,tlreac,tlsuscep,tlcond,shbus,shresis,shreac,ntl,nb,nsh);

[VM,VA,it]=NewtonRaphson(nmax,tol,itmax,ngn,nld,nb,bustype,genbus,loadbus,PGEN,

QGEN,QMAX,QMIN,PLOAD,QLOAD,YR,YI,VM,VA);

[PQsend,PQrec,PQloss,PQbus]=PQflows(nb,ngn,ntl,nld,genbus,loadbus,tlsend,tlrec,tlresis,

tlreac,

tlcond,tlsuscep,PLOAD,QLOAD,VM,VA);

[PQTCSCsend,PQTCSCrec]=TCSCPQpower(VA,VM,NTCSCFA,TCSCFAsend,

TCSCFArec,X);

VA=VA*180/pi;

MVAbase=100; % MVA base

Psend=real(PQsend)*MVAbase;

Qsend=imag(PQsend)*MVAbase;

Prec=real(PQrec)*MVAbase;

Qrec=imag(PQrec)*MVAbase;

Ploss=real(PQloss)*MVAbase;

Qloss=imag(PQloss)*MVAbase;

Pinjected=(real(PQbus)*MVAbase);

Pgen=[Pinjected(1,1) Pinjected(1,2) -PLOAD(1)*MVAbase Pinjected(1,3) Pinjected(1,4) Pinjected(1,5) Pinjected(1,6)];

Qinjected=(imag(PQbus)*MVAbase);

Qgen=[Qinjected(1,1) Qinjected(1,2) -QLOAD(1)*MVAbase Qinjected(1,3) Qinjected(1,4) Qinjected(1,5) Qinjected(1,6)];

disp ('ACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI      DELHI     NOIDA    NOIDA    NOIDA         DWARKA    FBAD')

disp ('    NOIDA      NAJAF   NAJAF     FBAD     GURGAON    FBAD         GURGAON')

disp ('    =====       =====    =====        ====       =======       =======     ========')

disp(Psend)

disp ('ACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====       =====     =====        ====      =======      =======   ========')

disp(Prec)

disp ('ACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI      DELHI     NOIDA     NOIDA    NOIDA         DWARKA    FBAD')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD         GURGAON')

disp ('    =====       =====      =====      ====        =======     =======      ========')

disp(Ploss)

disp ('REACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI      DELHI     NOIDA      NOIDA    NOIDA          DWARKA    FBAD')

disp ('    NOIDA      NAJAF   NAJAF      FBAD      GURGAON    FBAD          GURGAON')

disp ('    =====        =====    =====       ====        =======       =======       ========')

disp(Qsend)

disp ('REACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====      =====      =====       ====        =======     =======   ========')

disp(Qrec)

disp ('REACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI       DELHI   NOIDA      NOIDA    NOIDA         DWARKA    FBAD')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD        GURGAON')

disp ('    =====       =====     =====       ====       =======      =======     ========')

disp(Qloss)

disp ('NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA')

disp ('     =====      =====     =====       ====       =======    =======     ========')

disp(Pgen)

disp (' NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA')

disp ('    =====      =====     =====         ====       =======   =======    ========')

disp(Qgen)

TOTALGEN =(PQbus(1,1)+PQbus(1,2))*MVAbase;

TOTALGENERATION_ACTIVEPOWER =real(TOTALGEN)

TOTALGENERATION_REACTIVEPOWER =imag(TOTALGEN)

TOTAL_ACTIVE_LOAD=-(PLOAD(1)+PLOAD(2)+PLOAD(3)+PLOAD(4))*MVAbase

TOTAL_REACTIVE_LOAD=-(QLOAD(1)+QLOAD(2)+QLOAD(3)+QLOAD(4))*MVAbase

TOTAL_ACTIVEPOWER_LOSS=TOTALGENERATION_ACTIVEPOWER + TOTAL_ACTIVE_LOAD

TOTAL_REACTIVEPOWER_LOSS=TOTALGENERATION_REACTIVEPOWER + TOTAL_REACTIVE_LOAD

ACTIVE_POWER_INJECTED_IN_TCSC=(real(PQTCSCsend))*MVAbase

REACTIVE_POWER_INJECTED_IN_TCSC=imag(PQTCSCsend)*MVAbase

FINAL_FIRINGANGELE=FA

TOTAL_REACTANCE=X

TOTAL_ITERATION=it

%end of main TCSC program

SUMMARY OF OUTPUT :

ACTIVE POWER SENT FROM EACH BUS::::

DELHI      DELHI    NOIDA      NOIDA    NOIDA         DWARKA    FBAD

NOIDA      NAJAF   NAJAF      FBAD      GURGAON    FBAD         GURGAON

=====        =====   =====         ====        =======       =======     ========

88.7927      42.6632     25.5906     26.7005     54.1990          21.0060         7.1711

ACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD        GURGAON

=====        =====    =====        ====       =======      =======    ========

-86.2091     -40.8924   -25.1076    -26.1804    -52.9147        -20.9535       -7.0853

ACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI      DELHI    NOIDA      NOIDA    NOIDA          DWARKA    FBAD

NOIDA      NAJAF   NAJAF      FBAD      GURGAON    FBAD         GURGAON

=====        =====      =====       ====        =======       =======     ========

2.5836        1.7708      0.4830       0.5201      1.2843            0.0524          0.0858

REACTIVE POWER SENT FROM EACH BUS::::

DELHI      DELHI    NOIDA      NOIDA    NOIDA          DWARKA    FBAD

NOIDA      NAJAF   NAJAF      FBAD      GURGAON    FBAD          GURGAON

=====        =====      =====       ====        =======       =======     ========

74.3796       16.9521   -2.6660     -1.5331      5.6513            2.5142           0.4444

REACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====     =====      ====        =======     =======   ========

-73.1461     -17.3287   -0.0832      -1.0971     -4.9491         -4.3160       -5.0509

REACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI      DELHI    NOIDA      NOIDA    NOIDA          DWARKA    FBAD

NOIDA      NAJAF   NAJAF      FBAD      GURGAON    FBAD         GURGAON

=====        =====     =====       ====        =======       =======     ========

1.2335       -0.3766     -2.7493       -2.6302      0.7021          -1.8018          -4.6065

NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::

DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA

=====      =====     =====        ====        =======   =======       ========

131.4559    40.2810   -20.0000    -66.0000     -39.9629     -60.0000        21.0060

NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::

DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA

=====      =====     =====        ====       =======   =======       ========

91.3317    -61.6940    -10.0000    -17.4119    -4.9687     -10.0000           2.5142

TOTAL GENERATION_ACTIVE POWER =

171.7369

TOTAL GENERATION_REACTIVE POWER =

29.6377

TOTAL_ACTIVE_LOAD =

-165

TOTAL_REACTIVE_LOAD =

-40

TOTAL_ACTIVE POWER_LOSS =

6.7369

TOTAL_REACTIVE POWER_LOSS =

-10.3623

ACTIVE_POWER_INJECTED_IN_TCSC =

21.0000

REACTIVE_POWER_INJECTED_IN_TCSC =

2.4119

FINAL_FIRING ANGLE =

148.4675

TOTAL_REACTANCE =

-0.0216

TOTAL_ITERATION =

8

The output is superimposed on the given 6-bus network in Fig-8.2 for easy reference and modified figure is shown in Fig-8.3.

Gen-1

131.45             91.33

21.0

86.20

73.14

40.28        61.69

Gen-2

25.10

0.08

27.81

1.53

21.0    20.95

2.51       4.31

52.91

4.94

26.18

1.09

25.59

2.66

54.19

5.65

40.89

17.32

42.66

16.95

7.08

5.05

7.17

0.44

89.79

74.37

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

45 + j15

60 + j10

40 + j5

20 +j10

TCSC1

DWARKA - 6

Fig-8.3

Active and Reactive power flow shown at each bus for 6–bus network where one TCSC is used to control the power flow.

Active Power

Reactive Power

RESULT-1:

Fig 7.5  is modified and reproduced in Fig-8.3, in which one TCSC is connected between Najafgarh and Dwarka to control 21 MW of power flow from Najafgarh to Faridabad. The power flow solution is obtained in 8 iteration to a power mismatch tolerance of 1e-12. The power flow results are shown in fig-8.3.

Since the TCSC cannot generate active power, there is an increase in active power flow from DELHI bus to NAJAFGARH bus (i.e. from 42.00 MW to 42.66 MW).  At the same time there is increase of active power flow from NOIDA bus to NAJAFGARH bus (i.e from 24.56 MW to 25.59 MW). In total there is increase of active power flow from NAJAFGARH to FARIDABAD (i.e from 19.39 MW to 21 MW).

It should be remarked that transmission line from NAJAFGARH to FARIDABAD  is series compensated by the use of TCSC-1  and there is an increase of active power flow from 19.38 MW to 21 MW, which is just under 8% active power increase. Thus TCSC with firing angle control provides a good series compensation  in the  transmission line for controlling the active power flow.

8.3	POWER FLOW SOLUTION OF 7-BUS NETWORK:

The network shown in Fig-8.4 consists of two TCSC for controlling the power flow. One TCSC is connected in between Najafgarh and Dwarka. Other is connected in between Faridabad and Badarpur. The MATLAB code which is written for one TCSC  is now modified with additional data for TCSC-2 and executed. The power flows varies in the transmission line and it is different from the case used for one TCSC.

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

Tline-1

Tline-7

Tline-2

Tline-6

Tline-5

Tline-3

Tline-4

Gen-2

Gen-1

LOAD-1

LOAD-2

LOAD-4

LOAD-3

TCSC1

DWARKA-6

Fig-8.4

7-bus network where two TCSC is introduced in between Najafgarh bus to Dwarka bus and Faridabad to Badarpur

TCSC2

BADARPUR-7

DATA FOR 7-BUS NETWORK IN WHICH TCSC-1  AND TCSC-2 IS CONNECTED :

TRANSMISSION LINE DATA :

Total no of transmission line = 7

| Transmission Line | Fm | To | Resistance in p.u | Reactance in p.u | Susceptance in p.u |
| --- | --- | --- | --- | --- | --- |
| Tline-1 | Delhi | Noida | 0.02 | 0.06 | 0.06 |
| Tline-2 | Delhi | Najafgarh | 0.08 | 0.24 | 0.05 |
| Tline-3 | Noida | Najafgarh | 0.06 | 0.18 | 0.04 |
| Tline-4 | Noida | Faridabad | 0.06 | 0.18 | 0.04 |
| Tline-5 | Noida | Gurgaon | 0.04 | 0.12 | 0.03 |
| Tline-6 | Dwarka | Faridabad | 0.01 | 0.03 | 0.02 |
| Tline-7 | Badarpur | Gurgaon | 0.08 | 0.24 | 0.05 |

GENERATOR BUS DATA

Total no of Generator = 2

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power injected in p.u | Reactive power injected in p.u | Generators reactive power upper limits in p.u | Generators reactive power lower limit in p.u |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Delhi-1 | Slack Bus | 1.06 | 0 | unknown | unknown | 5 | -5 |
| Noida-2 | Generator PV Bus | 1.00 | ? | 0.4 | ? | 3 | -3 |

LOAD BUS DATA

Total no of load = 4

| Bus No | Bus Type | Nodal voltage in p.u | Nodal phase angle in p.u | Active power drawn in p.u | Reactive power drawn in p.u |
| --- | --- | --- | --- | --- | --- |
| Noida-2 | Load PQ Bus | ? | ? | 0.20 | 0.10 |
| Najafgarh-3 | Load PQ Bus | ? | ? | 0.45 | 0.15 |
| Faridabad-4 | Load PQ Bus | ? | ? | 0.40 | 0.05 |
| Gurgaon-5 | Load PQ Bus | ? | ? | 0.60 | 0.1 |

TCSC’s DATA

Total no of TCSC = 2

Data for TCSC-1

Connected between : From Najafgarh-3  to Dwarka-6

Capacitive reactance of TCSC -1= 9.375e-3

Inductive reactance of TCSC-1 = 1.625e-3

Initial Firing angle = 145 degree

Firing angle lower limit = 90 degree

Firing angle upper limit = 180 degree

Active power to be controlled = 0.21 p.u

Data for TCSC-2

Connected between : From Faridabad-4  to Badarpur-7

Capacitive reactance of TCSC -2= 9.375e-3

Inductive reactance of TCSC-2 = 1.625e-3

Initial Firing angle = 145 degree

Firing angle lower limit = 90 degree

Firing angle upper limit = 180 degree

Active power to be controlled = 0.22 p.u

General Parameters :

Maximum Iteration = 100,

Tolerance = 1e – 12

MATLAB PROGRAM—6.2

% Main  TCSC –FA Program for TCSC-1 and TCSC-2 to get the output of power flow solution of a given network

(MATLAB PROGRAM-6.1 is modified and some additional data is added for TCSC-2 and the portion of modified program is shown below)

% The seven buses in the network are numbered for the purpose of the power

% flow solution, as follows :

% DELHI = 1

% NOIDA = 2

% NAJAFGARH = 3

% FARIDABAD = 4

% GURGAON = 5

% DWARKA = 6

% BADARPUR = 7

nb=7;

bustype(1)=1;VM(1)=1.06;VA(1)=0;

bustype(2)=2;VM(2)=1;VA(2)=0;

bustype(3)=3;VM(3)=1;VA(3)=0;

bustype(4)=3;VM(4)=1;VA(4)=0;

bustype(5)=3;VM(5)=1;VA(5)=0;

bustype(6)=3;VM(6)=1;VA(6)=0;

bustype(7)=3;VM(7)=1;VA(7)=0;

%TRANSMISSION LINE DATA

% ntl = number of transmission lines

% tlsend = sending end of transmission line

% tlrec = receiving end of transmission line

% tlresis = series resistance of transmission line

% tlreac = series reactance of transmission line

% tlcond = shunt conductance of transmission line

% tlsuscep = shunt susceptance of transmission line

ntl=7;

tlsend(1)=1; tlrec(1)=2; tlresis(1)=0.02; tlreac(1)=0.06; tlcond(1)=0; tlsuscep(1)=0.06;

tlsend(2)=1; tlrec(2)=3; tlresis(2)=0.08; tlreac(2)=0.24; tlcond(2)=0; tlsuscep(2)=0.05;

tlsend(3)=2; tlrec(3)=3; tlresis(3)=0.06; tlreac(3)=0.18; tlcond(3)=0; tlsuscep(3)=0.04;

tlsend(4)=2; tlrec(4)=4; tlresis(4)=0.06; tlreac(4)=0.18; tlcond(4)=0; tlsuscep(4)=0.04;

tlsend(5)=2; tlrec(5)=5; tlresis(5)=0.04; tlreac(5)=0.12; tlcond(5)=0; tlsuscep(5)=0.03;

tlsend(6)=3; tlrec(6)=4; tlresis(6)=0.01; tlreac(6)=0.03; tlcond(6)=0; tlsuscep(6)=0.02;

tlsend(7)=4; tlrec(7)=5; tlresis(7)=0.08; tlreac(7)=0.24; tlcond(7)=0; tlsuscep(7)=0.05;

%TCSC DATA

NTCSCFA=1;

TCSCFAsend(1)=3;TCSCFArec(1)=6;Xc(1)=9.375e-3;Xl(1)=1.625e-3;

FA(1)=145;FALo(1)=90;FAHi(1)=180;Flow(1)=1;PSta(1)=1;Psp(1)=0.21;

TCSCFAsend(2)=4;TCSCFArec(2)=7;Xc(2)=12.375e-3;Xl(2)=.625e-3;

FA(2)=145;FALo(2)=90;FAHi(2)=180;Flow(2)=1;PSta(2)=1;Psp(2)=0.22;

% Main program

[YR,YI]=Ybus(tlsend,tlrec,tlresis,tlreac,tlsuscep,tlcond,shbus,shresis,shreac,ntl,nb,nsh);

[VM,VA,it,FA,X]=TCSCFANewtonRaphson(nmax,tol,itmax,ngn,nld,nb,bustype,genbus,loadbus,PGEN,QGEN,QMAX,QMIN,PLOAD,QLOAD,YR,YI,VM,...

VA,NTCSCFA,TCSCFAsend,TCSCFArec,Xc,Xl,FA,FALo,FAHi,Flow,PSta,Psp);

[PQsend,PQrec,PQloss,PQbus]=PQflows(nb,ngn,ntl,nld,genbus,loadbus,tlsend,tlrec,tlresis,

tlreac,tlcond,tlsuscep,PLOAD,QLOAD,VM,VA);

[PQTCSCsend,PQTCSCrec]=TCSCPQpower(VA,VM,NTCSCFA,TCSCFAsend,

TCSCFArec,X);

VA=VA*180/pi;

MVAbase=100; %base MVA

Psend=real(PQsend)*MVAbase;

Qsend=imag(PQsend)*MVAbase;

Prec=real(PQrec)*MVAbase;

Qrec=imag(PQrec)*MVAbase;

Ploss=real(PQloss)*MVAbase;

Qloss=imag(PQloss)*MVAbase;

Pinjected=(real(PQbus)*MVAbase);

Pgen=[Pinjected(1,1) Pinjected(1,2) -PLOAD(1)*MVAbase Pinjected(1,3) Pinjected(1,4) Pinjected(1,5) Pinjected(1,6) Pinjected(1,7)];

Qinjected=(imag(PQbus)*MVAbase);

Qgen=[Qinjected(1,1) Qinjected(1,2) -QLOAD(1)*MVAbase Qinjected(1,3) Qinjected(1,4) Qinjected(1,5) Qinjected(1,6) Qinjected(1,7)];

disp ('ACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI      DELHI     NOIDA      NOIDA    NOIDA         DWARKA    BPUR')

disp ('    NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD         GURGAON')

disp ('    =====       =====     =====        ====        =======      =======       ========')

disp(Psend)

disp ('ACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====        =====    =====       ====       =======      =======     ========')

disp(Prec)

disp ('ACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI      DELHI     NOIDA      NOIDA    NOIDA        DWARKA    BPUR')

disp ('    NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD       GURGAON')

disp ('    =====       =====     =====         ====      =======      =======     ========')

disp(Ploss)

disp ('REACTIVE POWER SENT FROM EACH BUS::::')

disp ('    DELHI       DELHI    NOIDA      NOIDA    NOIDA          DWARKA    BPUR')

disp ('    NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD         GURGAON')

disp ('    =====       =====    =====         ====        =======       =======     ========')

disp(Qsend)

disp ('REACTIVE POWER RECEIVED AT EACH BUS::::')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON')

disp ('    =====        =====    =====       ====       =======      =======    ========')

disp(Qrec)

disp ('REACTIVE POWER LOSS ON TRANSMISSION LINE::::')

disp ('    DELHI      DELHI    NOIDA      NOIDA    NOIDA        DWARKA    BPUR')

disp ('    NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD        GURGAON')

disp ('    =====       =====    =====        ====       =======      =======     ========')

disp(Qloss)

disp ('NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA BPUR')

disp ('    =====      =====     =====        =====        ====       =======       ======      ====')

disp(Pgen)

disp (' NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::')

disp ('    DELHI     NOIDA    NOIDA      NAJAF      FBAD     GURGAON   DWARKA BPUR')

disp ('    =====      =====      =====       =====       ====        =======       ======     =====')

disp(Qgen)

TOTALGENERATION_ACTIVEPOWER =(Pgen(1,1)+Pgen(1,2))

TOTALGENERATION_REACTIVEPOWER =(Qgen(1,1)+Qgen(1,2)+Qgen(1,5))

TOTAL_ACTIVE_LOAD=-(PLOAD(1)+PLOAD(2)+PLOAD(3)+PLOAD(4))*MVAbase

TOTAL_REACTIVE_LOAD=-(QLOAD(1)+QLOAD(2)+QLOAD(3)+QLOAD(4))*MVAbase

TOTAL_ACTIVEPOWER_LOSS=TOTALGENERATION_ACTIVEPOWER + TOTAL_ACTIVE_LOAD

TOTAL_REACTIVEPOWER_LOSS=TOTALGENERATION_REACTIVEPOWER + TOTAL_REACTIVE_LOAD

SUMMARY OF OUTPUTS:

ACTIVE POWER SENT FROM EACH BUS::::

DELHI       DELHI    NOIDA      NOIDA    NOIDA          DWARKA    BPUR

NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD         GURGAON

=====       =====     =====         ====       =======       =======     ========

89.2434      42.7349   25.4970      43.1498     38.3180          21.0033        22.9577

ACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF    NAJAF      FBAD     GURGAON    FBAD        GURGAON

=====      =====      =====        ====        =======       =======   ========

-86.6484    -40.9829   -25.0142    -41.8647    -37.6175        -20.9519      -22.3825

ACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI       DELHI    NOIDA      NOIDA    NOIDA         DWARKA    BPUR

NOIDA      NAJAF   NAJAF       FBAD     GURGAON    FBAD         GURGAON

=====        =====    =====        ====        =======       =======     ========

2.5951        1.7520     0.4828      1.2851       0.7005            0.0514          0.5752

REACTIVE POWER SENT FROM EACH BUS::::

DELHI      DELHI     NOIDA      NOIDA    NOIDA          DWARKA    BPUR

NOIDA      NAJAF   NAJAF       FBAD      GURGAON    FBAD         GURGAON

=====       =====     =====        ====          =======      =======     ========

74.2474      16.0179    -3.8013     -7.0318        10.0700          -0.1455        -4.4705

REACTIVE POWER RECEIVED AT EACH BUS::::

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD       GURGAON

=====        =====    =====       ====        =======     =======    ========

-72.9821     -16.4735    1.0360     6.4911       -11.0271      -1.6681         1.0271

REACTIVE POWER LOSS ON TRANSMISSION LINE::::

DELHI      DELHI   NOIDA      NOIDA    NOIDA      DWARKA    BPUR

NOIDA      NAJAF   NAJAF      FBAD     GURGAON    FBAD      GURGAON

=====        =====    =====        ====      =======    =======      ========

1.2653      -0.4556     -2.7653     -0.5408     -0.9571       -1.8136         -3.4434

NET ACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::

DELHI   NOIDA    NOIDA   NAJAF    FBAD    GURGAON  DWARKA   BPUR

=====    =====     =====     =====     ====       =======      ======       ====

131.9784  40.3164  -20.0000 -65.9971    -62.8167   -60.0000     21.0033     22.9577

NET REACTIVE POWER INJECTED/OUTAGE AT GENERATOR/LOAD BUS::::

DELHI     NOIDA    NOIDA      NAJAF      FBAD   GURGAON   DWARKA  BPUR

=====     =====      =====        =====        ====      =======       ======   =====

90.2652   -63.7452   -10.0000    -15.4376    4.8229     -10.0000        -0.1455     -4.4705

TOTAL GENERATION_ACTIVE POWER =

172.2948

TOTAL GENERATION_REACTIVE POWER =

31.3430

TOTAL_ACTIVE_LOAD =

-165

TOTAL_REACTIVE_LOAD =

-40

TOTAL_ACTIVE POWER_LOSS =

7.2948

TOTAL_REACTIVE POWER_LOSS =

-8.6570

21.0     20.95

0.14       1.66

25.01

1.03

21.0

86.64

72.98

40.31       63.74

Gen-2

Gen-1

131.97             90.26

43.14

7.03

37.61

11.02

41.86

6.49

25.49

3.80

38.31

10.07

40.98

16.47

42.73

16.01

22.38

1.02

22.95

4.47

89.24

74.24

DELHI

1

NAJAFGARH

3

FARIDABAD

4

NOIDA

2

GURGAON

5

45 + j15

60 + j10

40 + j5

20 +j10

TCSC1

DWARKA - 6

Fig-8.5

Active and Reactive power flow shown at each bus for

7–bus network where two TCSC is used to control the power flow.

TCSC2

BADARPUR-7

22.0

ACTIVE POWER

REACTIVE POWER

RESULT-2

From Fig-8.5, we observe that TCSC-1 provides series compensation in the transmission line between NAJAFGARH to FARIDABAD bus. This is because  active power flow from NAJAFGARH to FARIDABAD is increased from 19.39 MW (shown in fig 7.5) to 21 MW. At the same time the active power flow from DELHI to NAJAFGARH is increased from 42.00 MW to 42.73 MW and from NOIDA to NAJAFGARH is increased from 24.56 MW to 25.49 MW as TCSC doesn’t generate any active power.

Similarly from Fig-8.5, we observe that TCSC-2 provides series compensation in the transmission line between FARIDABAD to GURGAON. This is because active power flow from FARIDABAD to GURGAON is increased from 6.63 MW to 22 MW. At the same time the active power flow from NOIDA to FARIDABAD is increased from 27.81 MW to 27.81 MW and NOIDA to GURGAON is decreased from 54.75 MW to 38.31 MW as TCSC does not generate any active power.

Also power mismatch equation is satisfied  at each bus, after using  two TCSC. Thus from the analysis it is very clear that both TCSC provides effective series compensation  in the two different transmission line and specified amount of active power is controlled .

8.4	CONCLUSION:

From the Result-1 and Result-2, we reached at conclusion that, how effectively Thyristor-Controlled Series capacitor (TCSC) can control the active power flow between to buses. With the use of TCSC, a specified amount of power can be transferred from one bus to other as TCSC does not consume or generate active power.

9

CONCLUSION AND FURTHER

SCOPE OF WORK

9.1	SUMMARY OF WORK :

Objective  of the whole work is to control the power flow in the transmission line. This can be achieved by knowing the various parameters which are involved in power flow in the transmission line. In chapter 3RD and 4th  conventional method used to determine the various parameters. For each of the parameter, we have discussed how can we control the active and reactive power flow in the transmission line. For each parameter we have used PSCAD-4.0/MATLAB application software to analyze the power flow.

As Thyristor-Controlled Series Capacitor (TCSC) , is a series  compensator used in transmission line to control the active power flow, so in Chapter-5 it is discussed about the principle of series compensation and simulation block is used to verify the truth ness, how capacitor is effective element to reduce the series reactance. For this PSCAD-4.0 software is used.

In further discussion in Chapter-6, we have analyzed the characteristics of TCSC. By using PSCAD software and we come to know how effectively, TCSC can control the current  and active power flow in the transmission line by varying the firing angle of TCSC.

A practical electrical network is having large number of buses. Thus in this work, a 5-bus imaginary network is considered in Chapter-7 for finding the power flow solution. Newton-Raphson method is used to solve this network. By using MATLAB code for this network, power flow between each buses is determined. Power flow solution of this network satisfies the power mismatch equation at each bus.

In Chapter-8, Jacobian matrix is determined for 6-bus network in which one TCSC is used in between two buses. Again power flow solution is determined for this network and we come to know that it also satisfies the power mismatch equations at each bus. At the same time, a specified amount of active power is allowed flow between two buses by using the TCSC. In the next section again two TCSC is used to analyze the power flow in different transmission line. Here also MATLAB code is used for finding the power flow solution of given electrical network.

9.2	CONCLUSION :

From the execution of simulation block in PSCAD and MATLAB code, we reached at a conclusion that Thyristor-Controlled Series Capacitor is one of the fast acting power electronic controller which can provide current and power flow control in the transmission line by varying its firing angle. Thus TCSC can be used as a series capacitor to reduce the overall transmission line reactance . Depending on the enhancement of power transfer desired at that time, without affecting other system-performance criteria, series compensation can be varied by TCSC. Thus TCSC is one of  the important FACTS controller, which increases the overall power transfer capacity in the transmission line.

9.3	FURTHER SCOPE OF WORK :

Works on the topic never ends with limited application. It has much more area of application such as damping of the power swings from local and inter-area oscillations, Voltage regulation of local network , reduction of short-circuit current etc. Various research works are going on control interaction between multiple Thyristor -Controlled Series Capacitor (TCSC) . Also SVC-TCSC can be combined and used within power systems to enhance inter-area stability. In this work MATLAB code is used for 5-bus network for power flow solution. PSCAD-4.0 can also be used  for designing a physical 5-bus network to determine the exact power flow from one bus to another. Though in this discussion PSCAD-4.0  software is used for two bus system, but it can be used for large bus network. Further study can be made on the Influence of TCSC on Fault Component Distance Protection and Impact of TCSC on the Protection of Transmission Lines. Thus TCSC can be used in many fields.

Appendix-‘A’

MATLAB PROGRAM 2.1

%ANALYSIS OF ACTIVE AND REACTIVE POWER FLOW IN A LOSS LESS TRANSMISSION LINE

Vs=input ('line voltage= ');

Vr=Vs;

V=Vs;%assuming terminal voltage Vs=Vr=V

X=input('line reactance= ');

delta=(0:10:180)';

delta1=delta*pi/180;

l=length(delta1);

P=(V^2/X .* sin(delta1));%active power flow on transmission line

Q=(V^2/X).*(ones(l,1)-cos(delta1));% reactive power flow

result=[delta,P,Q];

disp('RESULT IS :::::')

disp ('    delta       P        Q  ')

disp(result)

plot(delta,P,delta,Q)

MATLAB PROGRAM-4.1

%ANALYSIS OF ACTIVE AND REACTIVE POWER FLOW

%WITH VARIATION OF FIRING ANGLE

Vs=input ('line voltage= ');

Vr=Vs;

V=Vs;

X=input('line reactance= ');

Xl=input ('inductive reactance of TCR= ');

Xc=input ('fixed capacitive impedance= ');

delta=input ('phase angle= ');%difference of phase angle between

%sending end and receiving end

delta1=(0:10:180)';%variation of load angle

alpha=(0:10:90)';%variation of firing angle

alpha1=alpha*pi/180;

l=length(alpha1);

k=length(delta1);

var1=ones(l,1)*pi;

var2=(var1-2.*alpha1-sin(2.*alpha1));

Xl_alpha=Xl*pi./(var2);%reactance of TCR

Xc_new=ones(l,1)*Xc;

r=(XT_alpha)./X;%compensating ratio

Xeq=(ones(l,1)*X-XT_alpha);%reactance of transmission line

%after compensation

Pc=(V^2*sin(delta*pi/180))./(Xeq);

Qc=(2*V^2/X)*(1-cos(delta*pi/180)).*(r./(ones(l,1)-r).^2);

result=[alpha,Pc,Qc,r];

disp('RESULT IS')

disp ('    alpha      Pc        Qc          r')

disp(result)

Pc1=(V^2/(1-r(1,1))*X).*sin(delta1.*pi/180);%active power for first element of r column matrix

Pc9=(V^2/(1-r(9,1))*X).*sin(delta1.*pi/180);%active power for 9th element of r column matrix

Pc10=(V^2/(1-r(10,1))*X).*sin(delta1.*pi/180);%active power for 10th element of 4 column matrix

Qc1=(2*V^2/X)*(r(1,1)/(1-r(1,1))^2).*(ones(k,1)-cos(delta1.*pi/180));%reactive power for

%first element of r column matrix

Qc9=(2*V^2/X)*(r(9,1)/(1-r(9,1))^2).*(ones(k,1)-cos(delta1.*pi/180));%reactive power for

%9th element of r column matrix

Qc10=(2*V^2/X)*(r(10,1)/(1-r(10,1))^2).*(ones(k,1)-cos(delta1.*pi/180));%reactive power for

%10th element of r column matrix

subplot(2,2,1),plot(alpha,Pc,alpha,Qc)

title ('ACTIVE POWER AND REACTIVE POWER vs FIRING ANGLE')

Xlabel ('firing angle')

ylabel ('P,Q')

subplot(2,2,2),plot(delta1,Pc1,delta1,Pc9,delta1,Pc10)

title('ACTIVE POWER vs LOAD ANGLE')

xlabel('load angle')

ylabel('active power(P) watt')

subplot(2,2,3),plot(delta1,Qc1,delta1,Qc9,delta1,Qc10)

title ('REACTIVE POWER vs LOAD ANGLE')

Xlabel('load angle')

ylabel('reactive power (Q) var')

Appendix – ‘B’

MATLAB PROGRAM-5.1

COMPUTER PROGRAM FOR POWER FLOW SOLUTION USING NEWTON-RAPHSON METHOD :

% Build up admittance matrix

function[YR,YI] = Ybus(tlsend,tlrec,tlresis,tlreac,tlsuscep,tlcond,shbus,shresis,shreac,ntl,nb,nsh);

YR=zeros(nb,nb);

YI=zeros(nb,nb);

%Transmission lines contribution

for l = 1:ntl   %numbering of transmission line

k = tlsend(1);  %sending end of transmission line

m = tlrec(1);  %receiving end of transmission line

denom =  tlresis(l)^2+tlreac(l)^2;

YR(k,k) = YR(k,k) + tlresis(l)/denom+0.5*tlcond(1);  %self conductance

YI(k,k) = YI(k,k) - tlreac(l)/denom +0.5*tlsuscep(1);  %self susceptance

YR(k,m) = YR(k,m) - tlresis(l)/denom;  %mutual conductance

YI(k,m) = YI(k,m) + tlreac(l)/denom;  %mutual susceptance

YR(m,k) = YR(m,k) - tlresis(l)/denom;

YI(m,k) = YI(m,k)+tlreac(l)/denom;

YR(m,m) = YR(m,m)+tlresis(l)/denom+0.5*tlcond(l);

YI(m,m) = YI(m,m)-tlreac(l)/denom+0.5*tlsuscep(l);

end

% Shunt elements contribution

for n = 1:nsh  %numbering of shunt connected

k = shbus(l);  %starting end of shunt

denom  = shresis(n)^2+shreac(n)^2;

YR(k,k) = YR(k,k)+shresis(n)/denom;

YI(k,k) = YI(k,k)-shreac(n)/denom;

end

%end of function Ybus

%Carry out iterative solution using the Newton-Raphson method

function[VM,VA,it] = NewtonRaphson(nmax,tol,itmax,ngn,nld,nb,bustype,genbus,

loadbus,PGEN,QGEN,QMAX,QMIN,PLOAD,QLOAD,YR,YI,VM,VA);

%GENERAL SETTINGS

D = zeros(1,nmax);

Flag = 0;

it = 1;

%CALCULATE NET POWERS

[PNET,QNET]=Netpowers(nb,ngn,nld,genbus,loadbus,PGEN,QGEN,PLOAD,QLOAD);

while (it < itmax & flag==0);

%CALCULATED POWERS

[PCAL,QCAL]=calculatedpowers(nb,VM,VA,YR,YI);

%CHECK FOR POSSIBLE GENERATOR'S REACTIVE POWERS LIMITS VIOLATIONS

[QNET,bustype]=GeneratorsLimits(ngn,genbus,bustype,QGEN,QMAX,QMIN,QCAL,

QNET,QLOAD,it,VM,nld,loadbus);

%POWER MISMATCHS

[DPQ,DP,DQ,flag]=PowerMismatches(nmax,nb,tol,bustype,flag,PNET,QNET,PCAL,

QCAL);

%JACOBIAN FORMATION

[JAC]=NewtonRaphsonJacobian(nmax,nb,bustype,PCAL,QCAL,VM,VA,YR,YI);

%SOLVE FOR THE STATE VARIABLES VECTOR

D=JAC\DPQ';

%UPDATE STATE VARIABLES

[VA,VM]=StateVariablesUpdates(nb,D,VA,VM);

it=it+1;

end

%End function Newton-Raphson

%Function to calculate the net scheduled powers

function[PNET,QNET]=Netpowers(nb,ngn,nld,genbus,loadbus,PGEN,QGEN,PLOAD,

QLOAD);

%CALCULATE NET POWERS

PNET=zeros(1,nb);

QNET=zeros(1,nb);

for ii = 1:ngn

PNET(genbus(ii))=PNET(genbus(ii))+PGEN(ii);

QNET(genbus(ii))=QNET(genbus(ii))+QGEN(ii);

end

for ii=1:nld

PNET(loadbus(ii))=PNET(loadbus(ii))-PLOAD(ii);

QNET(loadbus(ii))=QNET(loadbus(ii))-QLOAD(ii);

end

%end function Netpowers

%Function to calculate injected bus powers

function[PCAL,QCAL]=Calculatedpowers(nb,VM,VA,YR,YI);

%include all entries

PCAL=zeros(1,nb);

QCAL=zeros(1,nb);

for k= 1:nb

PSUM=0;

QSUM=0;

for m=1:nb

PSUM=PSUM+VM(k)*VM(m)*(YR(k,m)*cos(VA(k)-VA(m))-YI(k,m)*sin(VA(k)-VA(m)));

QSUM=QSUM+VM(k)*VM(m)*(YR(k,m)*sin(VA(k)-VA(m))-YI(k,m)*cos(VA(k)-VA(m)));

end

PCAL(k)=PSUM;

QCAL(k)=QSUM;

end

%End of function calculated powers

%Function to check whether or not solution is within generators limits

function[QNET,bustype]=GeneratorsLimits(ngn,genbus,bustype,QGEN,QMAX,QMIN,

QCAL,QNET,QLOAD,it,VM,nld,loadbus)

%CHECK FOR POSSIBLE GENERATOR'S REACTIVE POWERS LIMITS VIOLATIONS

if it > 2

flag2 = 0;

for ii=1:ngn

jj=genbus(ii);

if(bustype(jj) ==2)

if (QCAL(jj)>QMAX(ii))

QNET(genbus(ii))=QMAX(ii);

bustype(jj)=3;

flag2=1;

elseif (QCAL(jj) < QMIN(ii))

QNET(genbus(ii))=QMIN(ii);

bustype(jj)=3;

flag2=1;

end

if flag2==1

for ii=1:nld

if loadbus(ii)==jj

QNET(loadbus(ii))=QNET(loadbus(ii))-QLOAD(ii);

end

end

end

end

end

end

%End function GeneratorsLimits

%Function to compute power mismatches

function[DPQ,DP,DQ,flag]= powerMismatches(nmax,nb,tol,bustype,flag,PNET,QNET,PCAL,

QCAL);

%POWER MISMATCHES

DPQ=zeros(1,nmax);

DP=zeros(1,nb);

DQ=zeros(1,nb);

DP=PNET-PCAL;%active power mismatches

DQ=QNET-QCAL;%reactive power mismatches

%To remove the active and reactive powers contributions of the slack

%bus and reactive power of all PV buses

for k=1:nb

if (bustype(k)==1)

DP(k)=0;

DQ(k)=0;

elseif (bustype(k)==2)

DQ(k)=0;

end

end

%Re-arrange mismatch entries

kk=1;

for k = 1:nb

DPQ(kk)=DP(k);

DPQ(kk+1)=DQ(k);

kk=kk+2;

end

%Check for convergence

for k=1:nb*2

if (abs(DPQ) < tol)

flag=1;

end

end

%End function PowerMismatches

%Function to built the Jacobian matrix

function[JAC]=NewtonRaphsonJacobian(nmax,nb,bustype,PCAL,QCAL,VM,VA,YR,YI);

%JACOBIAN FORMATION

%Include all entries

JAC = zeros(nmax,nmax);

iii=1;

for k =1:nb

jjj =1;

for m=1:nb

if k = = m

JAC(iii,jjj) = -QCAL(k)-VM(k)^2*YI(k,k);

JAC(iii,jjj+1) = PCAL(k) + VM(k)^2*YR(k,k);

JAC(iii+1,jjj) = PCAL(k) - VM(k)^2*YR(k,k);

JAC(iii+1,jjj+1) =QCAL(k)-VM(k)^2*YI(k,k);

else

JAC(iii,jjj) = VM(k)*VM(m)*(YR(k,m)*sin(VA(k)-VA(m))-YI(k,m)*cos(VA(k)-VA(m)));

JAC(iii+1,jjj) =  -VM(k)*VM(m)*(YI(k,m)*sin(VA(k)-VA(m))+YR(k,m)*cos(VA(k)-VA(m)));

JAC(iii,jjj+1) =  -JAC(iii+1,jjj);

JAC(iii+1,jjj+1) = JAC(iii,jjj);

end

jjj = jjj+2

end

iii = iii+2

end

%Delete the voltage magnitude and phase angle equations of the slack

%bus and voltage magnitude equations corresponding to PV buses

for kk =1:nb

if (bustype(kk) = =1)

k = kk*2-1;

for m =1 : 2*nb

if k = =m

JAC(k,m) = 1;

else

JAC(k,m) =0;

JAC(m,k) =0;

end

end

end

if (bustype(kk) = =1) | (bustype(kk) = =2)

k = kk*2;

for m = 1: 2*nb

if k = = m

JAC(k,k)=1;

else

JAC(k,m)=0;

JAC(m,k)=0;

end

end

end

end

%End of function NewtonRaphsonJacobian

%Function to update state variables

function[VA,VM]=StateVariablesUpdates(nb,D,VA,VM);

iii=1;

for k =1:nb

VA(k)=VA(k)+D(iii);

VM(k)=VM(k)+D(iii+1)*VM(k);

iii=iii+2;

end

%End function StateVariableUpdating

%Function to calculate the power flows

function[PQsend,PQrec,PQloss,PQbus]=PQflows(nb,ngn,ntl,nld,genbus,loadbus,tlsend,tlrec,

tlresis,tlreac,tlcond,tlsuscep,PLOAD,QLOAD,VM,VA);

PQsend = zeros(1,ntl);

PQrec = zeros(1,ntl);

%Calculate active and reactive powers at the sending and receiving ends of

%transmission lines)

for l = 1:ntl

Vsend=(VM(tlsend(l))*cos(VA(tlsend(l))) + (VM(tlsend(l))*sin(VA(tlsend(l)))*j));

Vrec=(VM(tlrec(l))*cos(VA(tlrec(l))) + (VM(tlrec(l))*sin(VA(tlrec(l)))*j));

tlimped=tlresis(l)+tlreac(l)*j;

current=(Vsend-Vrec)/tlimped +Vrec*(tlcond(l)+tlsuscep(l)*j)*0.5;

PQsend(l)=Vsend*conj(current);

current=(Vrec-Vsend)/tlimped +Vrec*(tlcond(l)+tlsuscep(l)*j)*0.5;

PQrec(l)=Vrec*conj(current);

PQloss(l)=PQsend(l)+PQrec(l);

end

%Calculate active and reactive powers injections at buses

PQbus=zeros(1,nb);

for l=1:ntl

PQbus(tlsend(l))=PQbus(tlsend(l))+PQsend(l);

PQbus(tlrec(l))=PQbus(tlrec(l))+PQrec(l);

end

%Make corrections at generator buses, where there is load in order to get

%correct generators contributions

for ii=1:nld

jj =loadbus(ii);

for kk=1:ngn

ll=genbus(kk);

if jj = =ll

PQbus(jj)=PQbus(jj)+(PLOAD(ii)+QLOAD(ii)*j);

end

end

end

%End functions PQflows

Appendix-‘C’

MATLAB PROGRAM--6.1

COMPUTER PROGRAM FOR POWER FLOW CONTROL USING TCSC (THYRISTOR CONTROLLED SERIES CAPACITOR) :

% Build up admittance matrix

function[YR,YI]=Ybus(tlsend,tlrec,tlresis,tlreac,tlsuscep,tlcond,shbus,shresis,shreac,ntl,

nb,nsh); (This is same as mentioned in Appendix-B)

%Carry out itrative solution using the Newton-Raphson method where TCSC

%controller is used in the network

function[VM,VA,it,FA,X] =TCSCFA NewtonRaphson(nmax,tol,itmax,ngn,nld,nb,

bustype,genbus,loadbus,PGEN,QGEN,QMAX,QMIN,PLOAD,QLOAD,YR,YI,VM,…

VA,NTCSCFA,TCSCFAsend,TCSCFArec,Xc,X1,FA,FALo,FAHi,Flow,PSta,Psp);

%GENERAL SETTINGS

D=zeros(1,nmax);

flag=0;

it = 1;

%CALCULATE NET POWERS

[PNET,QNET]=Netpowers(nb,ngn,nld,genbus,loadbus,PGEN,QGEN,PLOAD,QLOAD);

while (it < itmax & flag = =0)

%CALCULATED POWERS

[PCAL,QCAL]=Calculatedpowers(nb,VM,VA,YR,YI);

%TCSC CALCULATED POWER

[PCAL,QCAL,X]=TCSCFACalculatePower(PCAL,QCAL,VM,VA,NTCSCFA,

TCSCFAsend,TCSCFArec,FA,Xc,Xl);

%POWER MISMATCHES

[DPQ,DP,DQ,flag]=PowerMismatches(nmax,nb,tol,bustype,flag,PNET,QNET,PCAL,

QCAL);

%check for convergence

if flag ==1

break

end

%JACOBIAN FORMATION

[JAC]=NewtonRaphsonJacobian(nmax,nb,bustype,PCAL,QCAL,VM,VA,YR,YI);

%MODIFICATION JACOBIAN FOR TCSC-FA-it calculate the TCSC equivalent

%reactance

[JAC]=TCSCFAJacobian(it,nb,JAC,VM,VA,NTCSCFA,TCSCFAsend,TCSCFArec,FA,Xc,Xl,

Flow,PSta);

%SOLVE JACOBIAN

D=JAC\DPQ';

%UPDATE STATE VARIABLES

[VA,VM]=StateVariablesUpdates(nb,D,VA,VM);

%UPDATE THE TCSC-FA VARIABLES

[FA]=TCSCFA_Updating(it,nb,D,NTCSCFA,FA,PSta);

%CHECK IMPEDANCE LIMITS

[FA]=TCSCFALimits(NTCSCFA,FA,FALo,FAHi,PSta);

it=it+1;

end

%End function TCSCFA Newton-Raphson

%Function to calculate injected bus powers by TCSC-FA

function[PCAL,QCAL]=CalculatePower(nb,VM,VA,YR,YI);

%include all entries

(This is same as mentioned in Appendix – B)

% Function to calculate injected bus powers by TCSC-FA

function[PCAL,QCAL,X]=TCSCFACalculatePower(PCAL,QCAL,VM,VA,NTCSCFA,

TCSCFAsend,TCSCFArec,FA,Xc,Xl);

for ii = 1:NTCSCFA

%Calculate Equivalent Reactance TCSCX

Xlc=Xc(ii)*Xl(ii)/(Xc(ii)-Xl(ii));

w=sqrt(Xc(ii)/Xl(ii));

C1=(Xc(ii)+Xlc)/pi;

C2=4*Xlc^2/(Xl(ii)*pi);

Ang=pi-FA(ii)*pi/180;

X(ii)= - Xc(ii)+C1*(2*Ang+sin(2*Ang))-C2*cos(Ang)^2*(w*tan(w*Ang)-tan(Ang));

Bmm= - 1/X(ii);

Bmk=1/X(ii);

for kk= 1:2

A=VA(TCSCFAsend(ii))-VA(TCSCFArec(ii));

Pcal =VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*sin(A);

Qcal = - VM(TCSCFAsend(ii))^2*Bmm - VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*cos(A);

PCAL(TCSCFAsend(ii))=PCAL(TCSCFAsend(ii))+Pcal;

QCAL(TCSCFAsend(ii))=QCAL(TCSCFAsend(ii))+Qcal;

if kk == 1

TCSC_PQsend(ii)=Pcal + j*Qcal;

else

TCSC_PQrec(ii)=Pcal + j*Qcal;

end

send = TCSCFAsend(ii);

TCSCFAsend(ii)=TCSCFArec(ii);

TCSCFArec(ii)=send;

end

end

%Function to compute power mismatches

function[DPQ,DP,DQ,flag]=powerMismatches(nmax,nb,tol,bustype,flag,PNET,QNET,

PCAL,QCAL);

(This is already mentioned in Appendix-B)

%Function to compute power mismatches with TCSC-FA

function[DPQ]=TCSCFAPowerMismatches(nb,DPQ,VM,VA,NTCSCFA,TCSCFAsend,TCSCFArec,X,Flow,it,Psp,PSta);

if it>1

for ii=1:NTCSCFA

if PSta(ii) ==1

Bmk=1/X(ii);

for kk=1:2

A=VA(TCSCFAsend(ii))-VA(TCSCFArec(ii));

Pcal=VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*sin(A);

if (Flow(ii)==1 & kk==1)|(Flow(ii)== -1 & kk==2)

DPQ(1,2*nb+ii) =Psp(ii)-Pcal;

break;

end

send = TCSCFAsend(ii);

TCSCFAsend(ii)=TCSCFArec(ii);

TCSCFArec(ii)=send;

end

else

DPQ(1, 2*nb+ii)=0;

end

end

end

%end of function TCSCFAPowerMismatches

%Function to built the Jacobian matrix

function[JAC]=NewtonRaphsonJacobian(nmax,nb,bustype,PCAL,QCAL,VM,VA,YR,YI);

%JACOBIAN FORMATION

%Include all entries

(This is already mentioned in Appendix-B)

%Function to add the TCSC-FA elements to Jacobian matrix

function[JAC]=TCSCFAJacobian(it,nb,JAC,VM,VA,NTCSCFA,TCSCFAsend,TCSCFArec,FA,Xc,Xl,Flow,PSta);

for ii = 1:NTCSCFA

%Calculate Equivalent Reactance TCSCX

Xlc=Xc(ii)*Xl(ii)/Xc(ii)-Xl(ii));

w=sqrt(Xc(ii)/Xl(ii));

C1=(Xc(ii)+Xlc)/pi;

C2=4*Xlc^2/(Xl(ii)*pi);

Ang=pi-FA(ii)*pi/180;

TCSCX= - Xc(ii)+C1*(2*Ang+sin(2*Ang))-C2*cos(Ang)^2*(w*tan(w*Ang)-tan(Ang));

%Calculate Reactance Derivative

DTCSCX1 = -2*C1*(1+cos(2*Ang));

DTCSCX2 = C2*(w^2*(cos(Ang)^2/cos(w*Ang)^2));

DTCSCX3 = -C2*(w*tan(w*Ang)*sin(2*Ang));

DTCSCX4 = C2*(tan(Ang)*sin(2*Ang)-1);

DTCSCX = DTCSCX1 + DTCSCX2 + DTCSCX3 + DTCSCX4;

Bmm= - 1/TCSCX;

Bmk=1/TCSCX;

for kk= 1:2

A=VA(TCSCFAsend(ii))-VA(TCSCFArec(ii));

Hkm= -VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmm*cos(A);

Nkm= VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmm*sin(A);

JAC(2*TCSCFAsend(ii)-1,2*TCSCFAsend(ii)-1)=JAC(2*TCSCFAsend(ii)-1,2*TCSCFAsend(ii)-1)-VM(TCSCFAsend(ii))^2*Bmm;

JAC(2*TCSCFAsend(ii)-1,2*TCSCFArec(ii)-1)=JAC(2*TCSCFAsend(ii)-1,2*TCSCFArec(ii)-1)-Hkm;

JAC(2*TCSCFAsend(ii)-1,2*TCSCFArec(ii))=JAC(2*TCSCFAsend(ii)-1,2*TCSCFArec(ii))-Nkm;

JAC(2*TCSCFAsend(ii),2*TCSCFAsend(ii))=JAC(2*TCSCFAsend(ii),2*TCSCFAsend(ii))-VM(TCSCFAsend(ii))^2*Bmm;

JAC(2*TCSCFAsend(ii),2*TCSCFArec(ii)-1)=JAC(2*TCSCFAsend(ii),2*TCSCFArec(ii)-1) + Nkm;

JAC(2*TCSCFAsend(ii),2*TCSCFArec(ii))=JAC(2*TCSCFAsend(ii),2*TCSCFArec(ii))-Hkm;

if it > 1

if PSta(ii)==1

A=VA(TCSCFAsend(ii))-VA(TCSCFArec(ii));

Ekm= -VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*sin(A)*Bmk^2*DTCSCX;

Fkm= -((VM(TCSCFAsend(ii))^2 - VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*cos(A)))*Bmk^2*DTCSCX;

if(Flow(ii)==1 & kk==1)|(Flow(ii)== -1 & kk == 2)

Hkm= -VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*cos(A);

Nkm= VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*sin(A);

JAC(2*nb+ii,2*TCSCFAsend(ii)-1) = -Hkm;

JAC(2*nb+ii,2*TCSCFAsend(ii)) = Nkm;

JAC(2*nb+ii,2*TCSCFArec(ii)-1) = Hkm;

JAC(2*nb+ii,2*TCSCFArec(ii)) = -Nkm;

JAC(2*nb+ii, 2*nb+ii) = Ekm;

end

JAC(2*TCSCFAsend(ii)-1,2*nb+ii) = Ekm;

JAC(2*TCSCFAsend(ii),2*nb+ii) = Fkm;

else

JAC(2*nb+ii,2*nb+ii)=1;

end

end

send=TCSCFAsend(ii);

TCSCFAsend(ii)=TCSCFArec(ii);

TCSCFArec(ii)=send;

end

end

%Function to update state variables

function[VA,VM]=StateVariablesUpdates(nb,D,VA,VM);

iii=1;

for k=1:nb

VA(k)=VA(k)+D(iii);

VM(k)=VM(k)+D(iii+1)*VM(k);

iii=iii+2;

end

%End function StateVariableUpdating

%Function to update TCSC-FA state variables

function [FA]=TCSCFA_Updating(it,nb,D,NTCSCFA,FA,PSta);

if it > 1

for ii = 1:NTCSCFA

if PSta(ii) ==1

FA(ii) = FA(ii)+D(2*nb+ii,1)*180/pi;

end

end

end

%CHECK IMPEDANCE LIMITS

function [FA] = TCSCFALimits(NTCSCFA,FA,FALo,FAHi,PSta);

for ii = 1:NTCSCFA

%Check impedance Limits

if FA(ii)<FALo(ii) | FA(ii) > FAHi (ii)

PSta(ii) = 0;

if FA(ii) < FALo(ii)

FA(ii)=FALo(ii);

elseif FA(ii) > FAHi (ii)

FA(ii) = FAHi(ii);

end

end

end

%Function to calculate the power flows in TCSC_FA controller

function[PQTCSCsend,PQTCSCrec]=TCSCPQpower(VA,VM,NTCSCFA,TCSCFAsend,

TCSCFrec,X);

for ii = 1:NTCSCFA

Bmm= - 1/X(ii);

Bmk=1/X(ii);

for kk= 1:2

A = VA(TCSCFAsend(ii))-VA(TCSCFArec(ii));

Ptcsc = VM(TCSCFAsend(ii))*VM(TCSCFArec(ii)*Bmk*sin(A);

Qtcsc = -VM(TCSCFAsend(ii))^2*Bmm-

VM(TCSCFAsend(ii))*VM(TCSCFArec(ii))*Bmk*cos(A);

if kk == 1

PQTCSCsend(ii,kk)=Ptcsc + j*Qtcsc;

else

PQTCSCrec(ii,kk)=Ptcsc + j*Qtcsc;

end

send = TCSCFAsend(ii);

TCSCFAsend(ii)=TCSCFArec(ii);

TCSCFArec(ii)=send;

end

end

REFERENCES :

- Hadi Saddat, “Power System Analysis (MATLAB concept)”, Tata McGraw-Hill, Edition,2002

- Muhammad H. Rashid, “Power Electronics (concept of Flexible AC Transmission Systems)”, Pearson Education-3rd Edition,2004

- Narain G. Hingorani / Laszlo Gyugyi, “Understanding FACTS”, IEEE press, 1st  Indian Edition,2001

- IJ Nagrath / DP Kothari, “Power System Engineering (concept of series and shunt compensation)”, Tata McGraw-Hill,2003

- C.L. Wadhwa, “Electrical Power Systems (compensation in power system)”, New Age International, 3rd Edition,2004

- P.Moore and P. Ashmole, “Flexible ac transmission systems : part 4-advanced FACTS controller,” Power Engineering Journal, April 1998,pp.95-100

- E Acha / VG Agelidis / T J E Miller, “Power Electronic Control in Electrical Systems”, Newnes Power Engineering Series,Ist Indian Edition,2006

- Fuerte-Esquivel, C.R.; Acha, E.; Ambriz-Perez, H.; “A thyristor controlled series compensator model for the power flow solution of practical power networks”, Power Systems, IEEE Transactions on Power Dlivery, Volume 15,  Issue 1,  Feb. 2000 Page(s):58 – 64

- Gama, C.; Tenorio, R.; “Improvements for power systems performance: modeling, analysis and benefits of TCSCs” , Power Engineering Society Winter Meeting, 2000. IEEE Volume 2,  23-27 Jan. 2000 Page(s):1462 - 1467 vol.2

- Xie Da; Niu Hui; Chen Chen; Wu Jishun, “An algorithm to control the power flow in large systems based on TCSC “ , Power System Technology, 1998. Proceedings. POWERCON '98. Volume 1,  18-21 Aug. 1998 Page(s):344 - 348 vol.1

- Geng Juncheng; Tong Luyuan; Ge Jun; Wang Zhonghong; “Mathematical   model for describing characteristics of TCSC”, Power System Technology, 2002. Proceedings. PowerCon 2002. Volume 3,  13-17 Oct. 2002 Page(s):1498 - 1502

- Abdel-Moamen, M.A.; Narayana Prasad Padhy, “Power flow control and transmission loss minimization model with TCSC for practical power networks”, Power Engineering Society General Meeting, 2003, Volume 2,  13-17 July 2003

- R. Mohan Mathur, Rajiv K. Varma; “ Thyristor-Based FACTS Controllers For Electrical Transmission Systems”, A John Wiley & Sons, Inc. Publication,2002

- Matsuki, J.; Ikeda, K.; Abe, M.; “Investigations of a thyristor-controlled series capacitor”, Industrial Electronics, Control, and Instrumentation, 1996., Proceedings of the 1996 IEEE IECON 22nd International Conference, Volume 2,  5-10 Aug. 1996 Page(s):683 – 688

- Persson, J.; Rouco, L.; Soder, L “Linear analysis with two linear models of a thyristor-controlled series capacitor”, Power Tech Conference Proceedings, 2003 IEEE Bologna, Volume 3,23-26 June 2003 Page(s):8pp

- IEEE Power Engineering Society, “FACTS Application”, IEEE press, New York, 1996

- William D. Stevenson, Jr. “Elements of Power System Analysis”, McGraw-Hill Series in Electrical Engineering, Fourth Edition,1982

- Persson, J.; Rouco, L.; Soder, L ,”Linear analysis with two linear models of a thyristor-controlled series capacitor”, Power Tech Conference Proceedings, 2003 IEEE Bologna

- Rudra Pratap Singh, “Intoduction to MATLAB”,Ist Edition,2004

- Guo Chulin, Tong Luyuan, Wang Zhonghang, “ Stability Control of TCSC between interconnected Power networks”, Power System Technology, 2002 proceedings, volume-3,13-17 Oct 2002, pages 1943-1946

- Stephen J. Chapman, “MATLAB Programming for Engineers”,Thomsan Learning, Third Edition,2004

- A. Ally, B.S Rigby, member, IEEE, “An Investigation into the Impact of a Thyristor Controlle Series Capacitor-Based Closed Loop Power Flow Controller under Fault Conditions”, IEEE AFRICON 2004, pages 675-681

- Xiaobo Tan, Luyuan Tong, “Characteristics and Firing angle control of Thyristor Controlled Series Compensation installations”, IEEE Conf 1998, pages 672-676

- R. Billinton, M. Fotuhi-Firuzaba and S.O. Faried, “ Power System Reliability Enhancement using a Thyristor Controlled Series Capacitor” , IEEE Transactions on Power Systems vol.14, No.1, February 1999.

- Zhao Xueqiang and Chen Chen,”Circuit Analysis of a Thyristor Controlled Series Compensation”, IEEE paper 1998, pages 1067-1072

SOFTWARE USED :

MATLAB-6.5

PSCAD-4.0